ll

STATE OF FLORIDA

DOMESTIC WASTEWATER FACILITY PERMIT

| PERMITTEE: | PERMIT NUMBER: | FL0026603 (Major) |
| --- | --- | --- |
|  | PA FILE NUMBER: | FL0026603-004-DW1P/NR |
| City of Largo | ISSUANCE DATE: | July 27, 2007 |
|  | EXPIRATION DATE: | July 26, 2012 |
| RESPONSIBLE AUTHORITY: |  |  |
| Mr. Irvin Kety |  |  |
| Environmental Services Director |  |  |
| P. O. Box 296 |  |  |
| Largo, FL 33779-0296 |  |  |

(727) 507-4475

FACILITY:

City of Largo AWWTF

5000 - 150th Avenue North

Clearwater, FL 33760

Pinellas County

Latitude: 27° 54’ 30” N      Longitude: 82° 42’ 10” W

This permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and applicable rules of the Florida Administrative Code (F.A.C.) and constitutes authorization to discharge to waters of the state under the National Pollutant Discharge Elimination System.  The above named permittee is hereby authorized to operate the facilities shown on the application and other documents attached hereto or on file with the Department and made a part hereof and specifically described as follows:

TREATMENT FACILITIES:

An existing 18.0 mgd Annual Average Daily Flow (AADF), Type I, advanced wastewater treatment plant utilizing a high-rate three-stage biological nutrient removal process, commonly referred to as the A2O process. The overall plant consists of three automatic bar screens, three grit removal basins, three primary clarifiers of 701,250 gallons total volume, three anaerobic basins of 549,780 gallons total volume, three anoxic basins of 392,700 gallons total volume, three aeration basins of 2,153,300 gallons total volume, six final clarifiers of  2,933,000 gallons total volume and a total surface area of 30,160 square feet, three traveling bridge type, shallow bed sand filters of  5,325 square feet total surface area, nine deep bed denitrification filters of 5,400 square feet total surface area, one post aeration basin of 440,000 gallons total volume, and two chlorine contact chambers of 690,000 gallons total volume. This facility is operated to provide advanced wastewater treatment (AWT) and high-level disinfected reclaimed water to a master reuse system within the City of Largo, the Carillon area and within the City of St. Petersburg, or to discharge effluent through an outfall to the stormwater system within Feather Sound and thence to Tampa Bay.

The on-site residual management facility has a capacity of 16 dry tons per day. The residual management facility consists of gravity thickening, sludge dewatering using belt-filter presses and a heat drying process for pelletization producing a marketable bulking agent used in fertilizer.

DISPOSAL:

Surface Water Discharge:  An existing 15.0 MGD annual average daily flow (AADF) permitted discharge to an unnamed ditch part of the stormwater system within Feather Sound (Class III fresh waters) which discharges to Old Tampa Bay at Discharge Location (D-001) which is approximately at a depth of approximately 2 feet.  The point of discharge is located approximately at latitude 27 o 53' 52" N, longitude 82 o 40' 13" W.

REUSE:

Land Application:  An existing 12.0 mgd AADF permitted capacity slow-rate public access (R001) Master Reuse System consisting of the limits of the City of Largo and including the Carillon area within the City of St. Petersburg and features three reclaimed water storage tanks  (5 mg at Starkey Road, 3 mg at Southwest and 10 mg at the WWTF).

IN ACCORDANCE WITH: The limitations, monitoring requirements and other conditions set forth in Pages 1 through 28 of this permit.

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.	Surface Water Discharges

- During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to discharge effluent from Outfall D-001 to an unnamed ditch, part of the stormwater system within Feather Sound (Class III fresh waters) which discharges to Old Tampa Bay. Such discharge shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

|  |  |  | Effluent Limitations |  |  |  | Monitoring Requirements |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter | Units | Max/Min | Annual Average | Monthly Average | Weekly Average | Single Sample | Monitoring Frequency | Sample Type | Monitoring Location Site Number | Notes |
| Flow (D-001) | MGD | Maximum | 15.0 | Report | - | - | Continuous | Recording flow meters and totalizers | FLW-03 | See Cond.I.A.4 |
| BOD, Carbonaceous 5 day, 20C | MG/L | Maximum | 5.0 | 6.25 | 7.5 | 10.0 | 7 Days/Week | 24-hour flow proportioned composite | EFA-01 |  |
| Solids, Total Suspended | MG/L | Maximum | 5.0 | 6.25 | 7.5 | 10.0 | 7 Days/Week | 24-hour flow proportioned composite | EFA-01 |  |
| Nitrogen, Total (as N) | MG/L | Maximum | 3.0 | 3.75 | 4.5 | 6.0 | 7 Days/Week | 24-hour flow proportioned composite | EFA-01 |  |
| Phosphorus, Total (as P) | MG/L | Maximum | 1.0 | 1.25 | 1.5 | 2.0 | 7 Days/Week | 24-hour flow proportioned composite | EFA-01 |  |
| Solids, Total Suspended | MG/L | Maximum | - | - | - | 5.0 | 7 Days/Week | Grab | EFB-01 |  |
| pH | SU | Range | - | - | - | 6.0 to 8.5 | Continuous | Meter | EFA-01 | See Cond.I.A.3 |
| Coliform, Fecal, % less than detection | PERCENT | Minimum |  | 75 |  |  | Monthly | Calculation | EFA-01 | See Cond.I.A.5 |
| Coliform, Fecal | #/100ML | Maximum |  |  |  | 25 | 7 Days/Week | Grab | EFA-01 | See Cond.I.A.5 |
| Oxygen, Dissolved (DO) | MG/L | Minimum | - | - | - | 5.0 | 7 Days/Week | Grab | EFD-01 |  |
| Total Residual Chlorine (For Disinfection) | MG/L | Minimum | - | - | - | 1.0 | Continuous | Meter | EFA-01 | See Cond.I.A.3, & 6 |
| Total Residual Chlorine (For Dechlorination) | MG/L | Maximum | - | - | - | 0.01 | 7 Days/Week | Grab | EFD-01 |  |
| Cyanide, Total (as CN) | UG/L | Maximum | - | - | - | 5.2 | Quarterly | Grab | EFD-01 |  |
| Dichlorobromomethane | UG/L | Maximum | 22.0 | - | - | - | Monthly | Grab | EFD-01 |  |
| Chronic Whole Effluent Toxicity | PERCENT | Minimum | - | - | - | 100 | Quarterly | 24-hour flow proportioned composite | EFD-01 | See Cond. I.A.8 |

- Effluent samples shall be taken at the monitoring site locations listed in Permit Condition I. A.  1. and as described below:

| Monitoring Location Site Number | Description of Monitoring Location |
| --- | --- |
| EFA-01 | After disinfection |
| EFB-01 | After filtration and prior to disinfection |
| EFD-01 | Prior to discharge to Feather Sound Outfall |
| FLW-03 | Flow to D-001 (FLW-01) - (FLW-02) |

- Hourly measurement of pH and total residual chlorine for disinfection during the period of required operator attendance may be substituted for continuous measurement. [Chapter 62-601, Figure 2]

- Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually. [62-601.200(17) and .500(6)]

- Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.  Note:  To report the “% less than detection,” count the number of fecal coliform observations that were less than detection, divide by the total number of fecal coliform observations in the month, and multiply by 100% (round to the nearest integer).  [62-600.440(5)(f)]

- A minimum of 1.0 mg/L total residual chlorine must be maintained for a minimum contact time of 15 minutes based on peak hourly flow. [62-600.440(5)(b) and (6)(b)]

## 7.	Chronic Whole Effluent Toxicity Testing

The permittee shall comply with the following whole effluent toxicity testing requirements and initiate the series of tests described below within 60 days of permit issuance, unless otherwise directed by the Department in writing, to evaluate chronic whole effluent toxicity of the discharge from outfall D-001 to Old Tampa Bay.

## Effluent Limitation

1.   A No Observed Effect Concentration (NOEC) of greater than or equal to 100% effluent in any routine test or any additional follow-up test shall constitute compliance with these permit conditions and Rule 62-302.530(62), F.A.C.

2.   A NOEC of less than 100% effluent in any routine test or additional test shall constitute a failure of the test.  The permittee shall notify the Department via telephone or e-mail within 24 hours of notification that a routine or additional test failed.

b.	Monitoring Frequency

The “routine” toxicity tests specified shall be conducted once every three months.

# c.   Routine Test Requirements

1.	The permittee shall conduct a daphnid, Ceriodaphnia dubia, Survival and Reproduction Test and a fathead minnow, Pimephales promelas, Larval Survival and Growth Test, concurrently.

2.	All test species, procedures and quality assurance criteria used shall be in accordance with Short-term Methods for Estimating the Chronic Toxicity of Effluents and Receiving Waters to Freshwater Organisms, 4th ed., EPA-821-R-02-013, or the most current edition.  Any deviation of the toxicity procedures outlined herein shall be submitted in writing to the Department for review and approval prior to use.

3.	The control water and dilution water used shall be moderately hard water as described in EPA-821-R-02-013, Section 7, or the most current edition.

4.	All routine tests shall be conducted using a control (0% effluent) and a minimum of five test concentrations: 100%, 50%, 25%, 12.5%, and 6.25% final effluent.

## d.  Sampling Requirements

1.	For each routine test or additional test required, a total of three 24-hour, flow-proportioned composite samples of final effluent shall be collected and used per the sampling protocol discussed in EPA-821-R-02-013, Section 8, or the most current edition.  The first sample shall be used to initiate the test.  The remaining two composite samples shall be collected according to the protocol and used as renewal solutions on Day 3 (48 hours) and Day 5 (96 hours) of the test.  If the duration of the discharge is less than 24-hours, the duration of discharge shall be documented on the chain of custody.

# e.  Additional Testing Requirements, if required

1.	If chronic toxicity (an NOEC of less than 100% effluent) is found in any routine test, the permittee shall conduct two additional definitive tests on each species indicating an NOEC of less than 100% effluent.

2.	Each additional test shall be conducted using a control (0% effluent) and a minimum of five dilutions: 100%, 50%, 25%, 12.5% and 6.25% effluent.  The dilution series may be modified in the second test to more accurately bracket the toxicity, such that at least two dilutions above (not to exceed 100% effluent) and two dilutions below the target concentration and a control (0% effluent) are run.  All test results shall be statistically analyzed according to the Appendices in EPA-821-R-02-013, or the most current edition.

3.	The first additional test shall be initiated within two weeks of the end of the failed routine test.  The second valid additional test shall be conducted one week thereafter.  The additional tests will be used to evaluate the persistence of the observed toxicity.

f.	Quality Assurance Requirements

1.	A standard reference toxicant quality assurance chronic toxicity test (SRT-QA) shall be conducted with each species used in the toxicity tests, either concurrently or no more than 30 days before the date of each routine or additional test conducted.  The SRT-QA data shall be submitted with each companion routine or additional test required.

2.	A test, routine or additional, will be considered valid only if control mortality does not exceed 20% for either test species and all test acceptability criteria are met as described in f.3 and f.6.  The results of any invalid test shall be submitted to the Department in conjunction with the results of the repeat test.

3.	Test acceptability criteria for each species are defined in EPA-821-R-02-013, Section 13.12 (C. dubia) and Section 11.12 (P. promelas) or the most current edition.

4.	If the mortality in the control (0% effluent) exceeds 20% for either species in any test, the test for that species (including the control) shall be invalidated and the test repeated.

5.	If, in any test, 100% mortality occurs in any test concentration prior to the end of the seven days, and control mortality is less than 20% at that time, that test (including the control) shall be terminated with the conclusion that the test failed.

6.	Routine and additional tests shall be evaluated for acceptability based on the observed dose-response relationship and the percent minimum significant difference (PMSD) as required by EPA-821-R-02-013, Sections 10.2.6 and 10.2.8, respectively.

## g.	Reporting Requirements

1.	Results from all tests shall be reported and submitted on the Discharge Monitoring Report (DMR) in the following manner:

- Routine Test Results: If the NOEC of a test species is less than 100% effluent, “<100%” should be entered on the DMR for that species.  If the NOEC of a test species is greater than or equal to 100% effluent, “>100%” should be entered.

-	Additional Test Results: Report the % effluent determined to be the NOEC endpoint of the test.

2.	A toxicity laboratory report for each routine test shall be prepared according to EPA-821-R-02-013, Section 10, Report Preparation and Test Review (or the most current edition) and mailed to the Department at the address in g.4.  within 30 days of the completion of the test.

3.  	For additional tests, a single toxicity report shall be prepared according to EPA-821-R-02-013, Section 10, or the most current edition, and mailed within 45 days of completion of the second additional, valid test.  If the routine test and any additional test fail to meet the criteria listed in “Effluent Limitations”, the permittee shall submit a plan to the Department within 60 days of completion of the additional test report as to the cause of the chronic toxicity and a plan to remedy the observed chronic toxicity.

4.     All toxicity reports shall be submitted to:

Department of Environmental Protection

Southwest District Office

13051 N. Telecom Parkway

Temple Terrace, FL 33637-0926

Telephone No.:  (813) 632-7600

8.	Ambient Monitoring

The permittee shall conduct an ambient monitoring program to evaluate the potential impacts of the discharge on the water quality of the receiving waters.  The monitoring described below shall be conducted on a quarterly basis during the first and fifth year of the permit and on a semi-annual basis (wet and dry season) during the second and fourth years of the permit.

- Sampling Locations:

- At the point of discharge.

- At a point located 15 feet north of Feather Sound Drive where it crosses over the weir downstream of Feather Sound Golf Course’s lake.  There must be flow from the lake’s weir into the creek during a sampling event.

- A reference site.

b.    Regime:  Each monitoring event shall be conducted during a discharge event from outfall.

c.	Sampling Depths:

Surface, mid-depth and bottom samples shall be collected at the two ambient sites (locations 2 and 3).

- Sampling Parameters:

(1)  Surface (locations 2 and 3):  pH, dissolved oxygen, temperature and salinity shall be measured at 0.1 meters below   the surface of the water.

(2)  Mid-depth (locations 2 and 3):  pH, dissolved oxygen, temperature, salinity, chlorophyll-a, turbidity, CBOD5, total Kjeldahl nitrogen, nitrite-nitrate nitrogen, total ammonia nitrogen, total phosphorus, ortho-phosphorus and fecal coliform bacteria.

(3)  Outfall (location 1; effluent):  pH, dissolved oxygen, temperature, salinity, total suspended solids, CBOD5, total Kjeldahl nitrogen, nitrite-nitrate nitrogen, total ammonia nitrogen, total phosphorus, ortho-phosphorus and fecal coliform bacteria.

(4)  Bottom (locations 2 and 3):  pH, dissolved oxygen, temperature and salinity shall be measured at 0.1 meters above the bottom.

e.	Secchi Depth:  Shall be measured at the two ambient sites (locations 2 and 3).

f.	Ambient Conditions:  Air temperature, rainfall, cloud cover and flow direction of receiving water shall be noted at each sampling location.

g.	Chain of Custody:  Times and dates of sampling as well as the samplers' names should be noted on the Chain of Custody (COC).

h.	Report:  A report shall be submitted quarterly in the first and fifth years and semi-annually in the second and fourth years, to the FDEP's Southwest District (in both printed and electronic formats) presenting the results and interpretations of the sampling events.  The report shall also include all chain of custody forms, laboratory results as reported by the laboratory and the physiochemical raw data sheets. [62-302.300]

B.	Reuse and Land Application Systems

- During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to direct reclaimed water to Reuse System R-001.  Such reclaimed water shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

|  |  |  | Reclaimed Water Limitations |  |  |  | Monitoring Requirements |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter | Units | Max/Min | Annual Average | Monthly Average | Weekly Average | Single Sample | Monitoring Frequency | Sample Type | Monitoring Location Site Number | Notes |
| Flow (R-001) | MGD | Maximum | 12.0 | Report | - | - | Continuous | Recording flow meters and totalizers | FLW-02 | See Cond.I.B.4 |
| BOD, Carbonaceous 5 day, 20C | MG/L | Maximum | 20.0 | 30.0 | 45.0 | 60.0 | 5 Days/Week | 24-hour flow proportioned composite | EFA-01 |  |
| Solids, Total Suspended | MG/L | Maximum | - | - | - | 5.0 | 7 Days/Week | Grab | EFB-01 |  |
| pH | SU | Range | - | - | - | 6.0 to 8.5 | Continuous | Meter | EFA-01 | See Cond.I.B.3 |
| Coliform, Fecal, % less than detection | PERCENT | Minimum |  | 75 |  |  | Monthly | Calculation | EFA-01 | See Cond.I.A.5 |
| Coliform, Fecal | #/100ML | Maximum |  |  |  | 25 | 7 Days/Week | Grab | EFA-01 | See Cond.I.A.5 |
| Total Residual Chlorine (For Disinfection) | MG/L | Minimum | - | - | - | 1.0 | Continuous | Meter | EFA-01 | See Cond.I.B.6 |
| Turbidity | NTU | Maximum | See Permit Condition I.B.7. |  |  |  | Continuous | Meter | EFB-01 |  |
| Giardia | CYSTS/100 L | Maximum | - | - | - | Report | Once every two years | Filtered | EFA-01 |  |
| Cryptosporidium | OOCYSTS/100 L | Maximum | - | - | - | Report | Once every two years | Filtered | EFA-01 |  |

- Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I. B.  1. and as described below:

| Monitoring Location Site Number | Description of Monitoring Location |
| --- | --- |
| EFA-01 | After disinfection |
| EFB-01 | After filtration and prior to disinfection |
| FLW-02 | Flow Meter to R-001 |

- Hourly measurement of pH during the period of required operator attendance may be substituted for continuous measurement.  [Chapter 62-601, Figure 2]

- Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]

- Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.  Note:  To report the “% less than detection,” count the number of fecal coliform observations that were less than detection, divide by the total number of fecal coliform observations in the month, and multiply by 100% (round to the nearest integer).  [62-600.440(5)(f)]

- The minimum total chlorine residual shall be limited as described in the approved operating protocol, such that the permit limitation for fecal coliform bacteria will be achieved.  In no case shall the total chlorine residual be less than 1.0 mg/L.  [62-600.440(5)(b); 62-610.460(2); and 62-610.463(2)]

- The maximum turbidity shall be limited as described in the approved operating protocol, such that the permit limitations for total suspended solids and fecal coliforms will be achieved.  [62-610.463(2)]

C.	Other Limitations and Monitoring and Reporting Requirements

- During the period beginning on the issuance date and lasting through the expiration date of this permit, the treatment facility shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

|  |  |  | Limitations |  |  |  | Monitoring Requirements |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Parameter | Units | Max/Min | Annual Average | Monthly Average | Weekly Average | Single Sample | Monitoring Frequency | Sample Type | Monitoring Location Site Number | Notes |
| Flow (Total Plant) | MGD | Maximum | 18.0 | Report | - | - | Continuous | Recording flow meters and totalizers | FLW-01 | See Cond.I.C.4 |
| Percent Capacity, (TMADF/Permitted Capacity) x 100 | PERCENT | Maximum | - | Report | - | - | Monthly | Calculation | FLW-01 |  |
| BOD, Carbonaceous 5 day, 20C | MG/L | Maximum | - | Report | - | - | Weekly | 24-hour flow proportioned composite | INF-01 | See Cond.I.C.3 |
| Solids, Total Suspended | MG/L | Maximum | - | Report | - | - | Weekly | 24-hour flow proportioned composite | INF-01 | See Cond.I.C.3 |
| Rainfall | INCHES | Maximum | - | Report (Mo. Total) | - | - | Monthly | Calculation | OTH-01 |  |

- Samples shall be taken at the monitoring site locations listed in Permit Condition I. C. 1 and as described below:

| Monitoring Location Site Number | Description of Monitoring Location |
| --- | --- |
| FLW-01 | Total Plant Flow Meter |
| INF-01 | Prior to treatment and ahead of RAS |
| OTH-01 | Rain Gauge |

- To the greatest extent possible based on the physical constraints of the headworks,  influent samples shall be collected so that they do not contain digester supernatant or return activated sludge, or any other plant process recycled waters.[62-601.500(4)]

- Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]

- The treatment facilities shall be operated in accordance with all approved operating protocols.  Only reclaimed water that meets the criteria established in the approved operating protocol may be released to system storage or to the reuse system.  Reclaimed water that fails to meet the criteria in the approved operating protocol shall be directed to the following permitted alternate discharge system: D-001. The operating protocol shall be reviewed and updated periodically to ensure continuous compliance with the minimum treatment and disinfection requirements.  Updated operating protocols shall be submitted to the Department for review and approval upon revision of the operating protocol and with each permit application.  [62-610.320(6) and 62-610.463(2)]

- Instruments for continuous on-line monitoring of total residual chlorine and turbidity shall be equipped with an automated data logging or recording device.  [62-610.463(2) & .865(8)(d)]

- Intervals between sampling for Giardia and Cryptosporidium shall not exceed two years.  Sampling results shall be reported on DEP Form 62-610.300(4)(a)4 which is attached to this permit.  This form shall be submitted to the Department and to DEP’s Reuse Coordinator in Tallahassee.  [62-610.463(4)]

- Parameters which must be monitored as a result of a surface water discharge shall be analyzed using a sufficiently sensitive method to assure compliance with applicable water quality standards and effluent limitations in accordance with 40 CFR (Code of Federal Regulations) Part 136.  Parameters which must be monitored as a result of a ground water discharge (i.e., underground injection or land application system) shall be analyzed in accordance with Chapter 62-601, F.A.C.   All monitoring shall be representative of the monitored activity. [62-620.320(6)]

- The sample collection, analytical test methods and method detection limits (MDLs) applicable to this permit shall be in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.  The list of Department established analytical methods, and corresponding MDLs (method detection limits) and PQLs (practical quantitation limits), which is titled “Florida Department of Environmental Protection Table as Required By Rule 62-4.246(4) Testing Methods for Discharges to Surface Water” is available at http://www.dep.state.fl.us/labs/guidance/index.htm.  The MDLs and PQLs as described in this list shall constitute the minimum acceptable MDL/PQL values and the Department shall not accept results for which the laboratory's MDLs or PQLs are greater than those described above unless alternate MDLs and/or PQLs have been specifically approved by the Department for this permit. Any method included in the list may be used for reporting as long as it meets the following requirements:

a)	The laboratory’s reported MDL and PQL values for the particular method must be equal or less than the corresponding method values specified in the Department’s approved MDL and PQL list;

b)	The laboratory reported MDL for the specific parameter is less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Parameters that are listed as “report only” in the permit shall use methods that provide a MDL, which is equal to or less than the applicable water quality criteria stated in 62-302, F.A.C.; and

c)	If the MDLs for all methods available in the approved list are above the stated permit limit or applicable water quality criteria for that parameter, then the method with the lowest stated MDL shall be used.

Where necessary, the permittee may request approval of alternate methods or for alternative MDLs or PQLs for any approved analytical method.  Approval of alternate laboratory MDLs or PQLs are not necessary if the laboratory reported MDLs and PQLs are less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Approval of an analytical method not included in the above-referenced list is not necessary if the analytical method is in accordance with 40 CFR 136.   [62-4.246, 62-160]

- The permittee shall provide safe access points for obtaining representative influent, reclaimed water, and effluent samples which are required by this permit. [62-601.500(5)]

- Monitoring requirements under this permit are effective on the first day of the second month following permit issuance.  Until such time, the permittee shall continue to monitor and report in accordance with previously effective permit requirements, if any.  During the period of operation authorized by this permit, the permittee shall complete and submit to the Department Discharge Monitoring Reports (DMRs) in accordance with the frequencies specified by the REPORT type (i.e., monthly, toxicity, quarterly, semiannual, annual, etc.) indicated on the DMR forms attached to this permit.  Monitoring results for each monitoring period shall be submitted in accordance with the associated DMR due dates below, unless specified elsewhere in the permit.

| REPORT Type | Monitoring Period | Due Date |
| --- | --- | --- |
| Monthly | first day of month – last day of month | 28th day of following month |
| Quarterly | January 1 - March 31 April 1 – June 30 July 1 – September 30 October 1 – December 31 | April 28 July 28 October 28 January 28 |
| Semiannual | January 1 – June 30 July 1 – December 31 | July 28 January 28 |
| Annual | January 1 – December 31 | January 28 |

DMRs shall be submitted for each required monitoring period including months of no discharge.  The permittee shall make copies of the attached DMR form and shall submit the completed DMR form to the Department by the 28th of the month following the month of operation at the address specified below:

Originals to:

Florida Department of Environmental Protection

Wastewater Compliance Evaluation Section, Mail Station 3551

Twin Towers Office Building

2600 Blair Stone Road

Tallahassee, Florida 32399-2400

Copies to:

Florida Department of Environmental Protection

Domestic Wastewater Program

Southwest District Office

13051 N. Telecom Parkway

Temple Terrace, FL 33637-0926

[62-620.610(18)][62-601.300(1),(2), and (3)]

12.	During the period of operation authorized by this permit, reclaimed water or effluent shall be monitored annually for the primary and secondary drinking water standards contained in Chapter 62-550, F.A.C., (except for asbestos, color, and corrosivity).  Twenty-four hour composite samples or grab samples where appropriate, shall be used to analyze reclaimed water or effluent for the primary and secondary drinking water standards.  These monitoring results shall be reported to the Department annually on the DMR.  During years when a permit is not renewed, a certification stating that no new non-domestic wastewater dischargers have been added to the collection system since the last reclaimed water or effluent analysis was conducted may be submitted in lieu of the report.  The annual reclaimed water or effluent analysis report or the certification shall be completed and submitted in a timely manner so as to be received by the Department by June 28 of each year.  Approved analytical methods identified in Rule 62-620.100(3)(j), F.A.C., shall be used for the analysis.  If no method is included for a parameter, methods specified in Chapter 62-550, F.A.C., shall be used.  [62-601.300(4)][62-601.500(3)][62-610.300(4)]

13.	The permittee shall submit an Annual Reuse Report using DEP Form 62-610.300(4)(a)2. on or before January 1 of each year.  [62-610.870(3)]

14.	The permittee shall maintain an inventory of storage systems.  The inventory shall be submitted to the Department at least 30 days before reclaimed water will be introduced into any new storage system.  The inventory of storage systems shall be attached to the annual submittal of the Annual Reuse Report.  [62-610.464(5)]

15.	Unless specified otherwise in this permit, all reports and other information required by this permit, including 24-hour notifications, shall be submitted to or reported to, as appropriate, the Department's Southwest District Office at the address specified below:

Southwest District Office

13051 N. Telecom Parkway

Temple Terrace, FL 33637-0926

Phone Number - 813-632-7600

FAX Number -  813-632-7662

Email – DWSWD@DEP.STATE.FL.US

All FAX copies shall be followed by original copies.  All reports and other information shall be signed in accordance with the requirements of Rule 62-620.305, F.A.C.  [62-620.305]

II.	RESIDUALS MANAGEMENT REQUIREMENTS

- The method of residuals use or disposal by this facility is distribution and marketing, transport to a Residual Management Facility or disposal in a Class I or II solid waste landfill.  Transportation of the residuals to an alternative RMF does not require a permit modification, however, use of an alternative RMF requires a copy of the agreement pursuant to Rule 62-640.880(1)(c), F.A.C., along with a written notification to the Department at least 30 days before transport of the residuals.

- The permittee shall be responsible for proper treatment, management, use, and land application or disposal of its residuals.  [62-640.300(5)]

- The permittee shall not be held responsible for treatment, management, use, or land application violations that occur after its residuals have been accepted by a permitted residuals management facility with which the source facility has an agreement in accordance with Rule 62-640.880(1)(c), F.A.C., for further treatment, management, use or land application.  [62-640.300(5)]

- Disposal of residuals, septage, and other solids in a solid waste landfill, or disposal by placement on land for purposes other than soil conditioning or fertilization, such as at a monofill, surface impoundment, waste pile, or dedicated site, shall be in accordance with Chapter 62-701, F.A.C.  [62-640.100(6)(k)3 & 4]

- The domestic wastewater residuals for this facility are classified as Class AA.

- The permittee shall achieve Class A pathogen reduction by meeting the pathogen reduction requirements in section 503.32(a)(7) (Use of PFRP - Heat Drying) of Title 40 CFR Part 503, revised as of October 25, 1995.  [62-640.600(1)(a)]

- The permittee shall achieve vector attraction reduction by meeting the vector attraction reduction requirements in section 503.33(b)(8) (Reduce moisture content of biosolids with unstabilized solids to at least 90%) of Title 40 CFR Part 503, revised as of October 25, 1995.  [62-640.600(2)(a)]

- Treatment of liquid residuals or septage for the purpose of meeting the pathogen reduction or vector attraction reduction requirements set forth in Rule 62-640.600, F.A.C., shall not be conducted in the tank of a hauling vehicle.  Treatment of residuals or septage for the purpose of meeting pathogen reduction or vector attraction reduction requirements shall take place at the permitted facility.  [62-640.400(8)]

- The permittee shall sample and analyze the Class AA residuals to monitor the parameters listed in the table below at least monthly.  All samples shall be representative of the residuals used, land applied, or distributed and marketed, and shall be taken after final treatment of the residuals but before use, land application, or distribution and marketing.

| Parameter | Ceiling Concentrations (Single Sample) | Class AA Parameter Concentrations (Monthly Average) |
| --- | --- | --- |
| Total Nitrogen | (Report only) % dry weight | In Accordance with AUP |
| Total Phosphorus | (Report only) % dry weight | (Report only) % dry weight |
| Total Potassium | (Report only) % dry weight | (Report only) % dry weight |
| Arsenic | 75 mg/kg dry weight | 41 mg/kg dry weight |
| Cadmium | 85 mg/kg dry weight | 39 mg/kg dry weight |
| Copper | 4300 mg/kg dry weight | 1500 mg/kg dry weight |
| Lead | 840 mg/kg dry weight | 300 mg/kg dry weight |
| Mercury | 57 mg/kg dry weight | 17 mg/kg dry weight |
| Molybdenum | 75 mg/kg dry weight | Not applicable |
| Nickel | 420 mg/kg dry weight | 420 mg/kg dry weight |
| Selenium | 100 mg/kg dry weight | 100 mg/kg dry weight |
| Zinc | 7500 mg/kg dry weight | 2800 mg/kg dry weight |
| pH | (Report only) standard units | (Report only) standard units |
| Total Solids | (Report only) % | (Report only) % |

[62-640.650(1), 62-640.700(1), 62-640.700(3)(b), and 62-640.850(3)]

- Residuals samples shall be taken at the monitoring site locations described below:

| Monitoring Location Site Number | Description of Monitoring Location |
| --- | --- |
| RMP-AA | Storage Bins |

- Sampling and analysis shall be conducted in accordance with Title 40 CFR Part 503, section 503.8 and the U.S. Environmental Protection Agency publication - POTW Sludge Sampling and Analysis Guidance Document, 1989.  In cases where disagreements exist between Title 40 CFR Part 503, section 503.8 and the POTW Sludge Sampling and Analysis Guidance Document, the requirements in Title 40 CFR Part 503, section 503.8 will apply. [62-640.650(1), 62-640.700(1), 62-640.700(3)(b), and 62-640.850(3)]

- Grab samples shall be used for pathogens and determinations of percent volatile solids.  Composite samples shall be used for metals.  [62-640.650(1)(e)]

- Residuals shall not be land applied if a single sample result for any parameter exceeds the ceiling concentrations given in this permit.  Residuals shall not be distributed and marketed if the monthly average of sample results for any parameter exceeds the Class AA parameter concentrations given in this permit.  Monthly averages of parameter concentrations shall be determined by taking the arithmetic mean of all sample results for the month.  [62-640.650(1)(f)]

- The permittee shall submit the results of all residuals monitoring with the permittee’s Discharge Monitoring Report under Chapter 62-601, F.A.C.  The analytical results from each sampling event shall be submitted with the report for the month in which the sampling event occurs.  [62-640.650(3)(a)&(e)]

- Only domestic wastewater residuals that meet Class AA standards may be sold or given away in a distribution and marketing program. The distribution and marketing of residuals shall be conducted in accordance with Chapter 62-640, F.A.C.  [62-640.850]

- The permittee shall submit a Monthly Residuals Distribution and Marketing Report to the Domestic Wastewater Section of the Department on Form 62-640.210(2)(c) by the 28th day of the month following the reporting month.  The report shall be submitted to the following address:

Florida Department of Environmental Protection
Domestic Wastewater Section, Mail Station 3540
Twin Towers Office Building
2600 Blair Stone Road
Tallahassee, Florida 32399-2400

[62-640.850(4)]

- The permittee shall make the following information available to users by product labels or other means:

a.	The name and address of the facility or person that produced the Class AA residuals;
b.	A statement that the residuals or residuals product meets the criteria of Rule 62-640.850(3), F.A.C.;
c.	A recommendation that residuals be applied at a rate that does not exceed the agronomic rate; and
d.	The following residuals analysis information (dry weight basis):
	Total Nitrogen (%)
	Total Phosphorus (%)
	Total Potassium (%)

[62-640.850(5)]

18.	The permittee shall be responsible for proper treatment, management, use, and land application of residuals accepted from source facilities.  [62-640.880(1)(a)]

19.	The permittee shall enter into a written agreement with each source facility that it intends to receive residuals from.  The agreement shall address the quality and quantity of the residuals accepted by the permittee.  The agreement shall include a statement, signed by the permittee, as to the availability of sufficient permitted capacity to receive the residuals from the source facility, and indicating that the permittee will continue to operate in compliance with the requirements of its permit.  The agreement shall also address responsibility during transport of residuals between the facilities.  The permittee shall submit a copy of this agreement to the Southwest District Office at least 30 days before transporting residuals from the source facility to the permittee.    [62-640.880(1)(c)]

20.	The permittee shall keep hauling records to track the transport of residuals between facilities.  The hauling records shall contain the following information:

| Source Facility | Residuals Management Facility or Treatment Facility |
| --- | --- |
| 1. Date and Time Shipped | 1. Date and Time Received |
| 2. Amount of Residuals Shipped | 2. Amount of Residuals Received |
| 3. Degree of Treatment (if applicable) | 3. Name and ID Number of Source Facility |
| 4. Name and ID Number of Residuals | 4. Signature of Hauler |
| Management Facility or Treatment Facility | 5. Signature of Responsible Party at Residuals Management Facility or Treatment Facility |
| 5. Signature of Responsible Party at Source Facility |  |
| 6. Signature of Hauler and Name of Hauling Firm |  |

These records shall be kept for five years and shall be made available for inspection upon request by the Department.  A copy of the hauling records information maintained by the source facility shall be provided upon delivery of the residuals to the residuals management facility or treatment facility.  The permittee shall report to the Department within 24 hours of discovery any discrepancy in the quantity of residuals leaving the source facility and arriving at the residuals management facility or treatment facility.  [62-640.880(4)]

III.	GROUND WATER REQUIREMENTS

Construction Requirements

- The permittee shall give at least 72-hours notice to the Department's Southwest District Office, prior to the installation of any monitoring wells detailed in this permit.  [62-4.070]

- The QUARTERLY sampling and analysis of all new ground water monitoring wells shall begin upon proper completion of the GWMP well system.  The wells shall be sampled for the parameters identified in Permit Condition III.13 and in accordance to the Department’s “Standard Operating Procedures For Laboratory Operations and Sample Collection Activities,” DEP-SOP-001/01, FS 2200 Ground water Sampling, January 1, 2002. [62-522.600(1) , (11)(a),  and (b)]

- Prior to construction of new ground water monitoring wells, a soil boring shall be made at each new monitoring well location in order to establish the well depth and screen interval.  [62-522.900(3)]

- Within thirty days after completion of construction of the ground water monitoring wells, a properly scaled figure depicting monitor well locations (active and abandoned) with identification numbers shall be submitted.   The figure shall also include (or attached) the monitoring well, top of casing and ground surface elevations referenced to National Geodetic Vertical Datum (NGVD) to the nearest 0.1 foot, along with monitor well location latitude and longitude to the nearest 0.1 second. 62-610.412 (c)

- Within thirty days after completion of construction of the ground water monitoring wells, well completion reports shall be sent to the Domestic Wastewater Section, FDEP Southwest District Office.  The information is to be submitted on the attached form for each well, DEP Form 62-522.900(3), Monitor Well Completion Report.  [62-522.900(3)]

- Within 30 days of completion of construction of new ground water monitor wells, the Department requests that the permittee submit the following information for each monitor well :

a.   A copy of the Florida Water Management District (WMD) , State of Florida Permit  Application to Construct, Repair, Modify or Abandon a Well, Form 41.10-410(1),  and

b.  A copy of the WMD Well Completion Report, Form 41.10-410(2),  62-610.412(2)(b)

- Prior to the application of effluent to the reuse/disposal site, the permittee shall sample all new ground water monitoring wells for the Primary and Secondary Drinking Water parameters included in Rule 62-550, Florida Administrative Code, Public Drinking Water Systems (excluding asbestos, acrylamide dioxin, butachlor and epichlorohydrin), and EPA Methods 601 and 602. [62-520.400 and 62-520.420]  [62-522.300(1), and 62-522.600(3)(A)]

- The permittee shall coordinate any expansion of the Part III public access reuse system with the Southwest District Domestic Waste Permitting Section and shall propose additional ground water monitoring that may be required due to such expansion.  All new ground water monitoring wells that may subsequently be required shall be identified in a revision to the GWMP and shall be installed within 90 days of Department approval of the GWMP revision.  The permittee shall apply for a major revision to this permit to incorporate the selected wells and to provide appropriate DMR section D pages. [62-522.600(11)(C) and 62-610.320(3)]

Operational Requirements

- For the Part III Public Access system, all ground water quality criteria specified in Chapter 62-520, F.A.C., shall be met at the edge of the zone of discharge.  The zone of discharge shall extend horizontally 100 feet from the application site or to user’s site property line, whichever is less, and vertically to the base of the surficial aquifer.  [62-520.200(23)]  [62-522.400 and 62-522.410]

- The ground water minimum criteria specified in Rule 62-520.400 F.A.C., shall be met within the zone of discharge.  [62-520.400 and 62-520.420(4)]

- During the period of operation authorized by this permit, the permittee shall sample ground water in accordance with this permit and the approved ground water monitoring plan prepared in accordance with Rule 62-522.600, F.A.C.  [62-522.600][62-610.463, ]

- The following monitoring wells shall be sampled in accordance with the monitoring frequencies specified in Permit Condition III.8. for Reuse System R-001.  Quarterly sampling must be reasonably spaced to be representative of potentially changing conditions.

| Monitoring Well ID | Alternate Well Name and/or Description of Monitoring Location | Depth (Feet) | Aquifer Monitored | New or Existing |
| --- | --- | --- | --- | --- |
| MWC-01 | Largo Central Park Compliance |  | Surficial | new |
| MWC-03 | AIRCO GC Compliance (AIRCO-3) |  | Surficial | existing |
| MWC-04 | AIRCO GC Compliance (AIRCO-2) |  | Surficial | existing |
| MWC-05 | AIRCO GC Compliance (AIRCO-1) |  | Surficial | existing |
| MWB-01 | Largo Central Park Background |  | Surficial | new |
| MWB-02 | AIRCO GC Background (AIRCO-4) |  | Surficial | existing |
| MWC-02 | Largo Central Park Compliance |  | Surficial | existing |
| MWB-03 | Highlands Park CC Background (HMW-1) |  | Surficial | existing |
| MWC-06 | Highlands Park CC Complaince (HMW-2) |  | Surficial | existing |
| MWC-07 | Largo Municipal GC Compliance (LMGC-1) |  | Surficial | existing |
| MWC-08 | Largo Municipal GC Compliance (LMGC-2) |  | Surficial | existing |

MWB = Background;  MWI = Intermediate;  MWC = Compliance

[62-522.600 and 62-610.463]

- The following parameters shall be analyzed for each of the monitoring well identified in Permit Condition III. 12:

| Parameter | Compliance Well Limit | Units | Sample Type | Monitoring Frequency |
| --- | --- | --- | --- | --- |
| Water Level Relative to NGVD | Report | FEET | In-situ | Quarterly |
| Nitrogen, Nitrate, Total (as N) | 10 | MG/L | Grab | Quarterly |
| Solids, Total Dissolved (TDS) | 500 | MG/L | Grab | Quarterly |
| Arsenic, Total Recoverable | 10 | UG/L | Grab | Quarterly |
| Chloride (as Cl) | 250 | MG/L | Grab | Quarterly |
| Cadmium, Total Recoverable | 5 | UG/L | Grab | Quarterly |
| Chromium, Total Recoverable | 100 | UG/L | Grab | Quarterly |
| Lead, Total Recoverable | 15 | UG/L | Grab | Quarterly |
| Coliform, Fecal | 4 | #/100ML | Grab | Quarterly |
| pH | 6.5 to 8.5 | SU | In-situ | Quarterly |
| Sulfate, Total | 250 | MG/L | Grab | Quarterly |
| Turbidity | Report | NTU | In-situ | Quarterly |
| Sodium, Total Recoverable | 160 | MG/L | Grab | Quarterly |
| Specific Conductance | Report | UMHO/CM | In-situ | Quarterly |
| Temperature (C), Water | Report | DEG.C | In-situ | Quarterly |
| Oxygen, Dissolved (DO) | Report | MG/L | In-situ | Quarterly |

[62-522.600(11)(b)] [62-601.300(3), 62-601.700, and Figure 3 of 62-601][62-601.300(6)] [62-520.300(9)]

- If the concentration for any constituent listed in Permit Condition III.13. in the natural background quality of the ground water is greater than the stated maximum, or in the case of pH is also less than the minimum, the representative natural background quality shall be the prevailing standard.  [62-520.420(2)]

- In accordance with Part D of Form 62-620.910(10), water levels shall be recorded before evacuating wells for sample collection.  Elevation references shall include the top of the well casing and land surface at each well site (NGVD allowable) at a precision of plus or minus 0.1 foot.  [62-610.463(3)(a), ]

- Ground water monitoring wells shall be purged prior to sampling to obtain representative samples.  [62-601.700(5)]

- Analyses shall be conducted on unfiltered samples, unless filtered samples have been approved by the Department's Southwest District Office as being more representative of ground water conditions.  [62-520.300(9)]

- Ground water monitoring parameters shall be analyzed in accordance with Chapter 62-601, F.A.C.  [62-620.610(18)]

- Ground water monitoring test results shall be submitted on Part D of Form 62-620.910(10). For reuse or land application projects, results shall be submitted with the DMR for each month listed in the following schedule.  The submitted results shall be for each year during the period of operation allowed by this permit in accordance with Permit Condition I.C.11.  [62-522.600(10) and (11)(b)]  [62-601.300(3), 62.601.700, and Figure 3 of 62-601] [62-620.610(18)]

| SAMPLE PERIOD | REPORT DUE DATE |
| --- | --- |
| January - March | April 28 |
| April - June | July 28 |
| July - September | October 28 |
| October - December | January 28 |

20.	If any monitoring well becomes damaged or cannot be sampled for some reason, the permittee shall notify the Department's Southwest District Office immediately and a written report shall follow within seven days detailing the circumstances and remedial measures taken or proposed.   Repair or replacement of monitoring wells shall be approved in advance by the Department's Southwest District Office.  [62-522.600][62-4.070(3)]

21.	All piezometers and monitoring wells not part of the approved ground water monitoring plan are to be plugged and abandoned in accordance with Rule 62-532.500(4), F.A.C., unless there is intent for their future use.  [62-532.500(4)]

IV.	ADDITIONAL REUSE AND LAND APPLICATION REQUIREMENTS

Part III Public Access System (R-001)

- Use of reclaimed water is authorized within the general service area consisting of the limits of the City of Largo and including the Carillon area within the City of St. Petersburg.  The following uses of reclaimed water are authorized within this general service area:  Athletic Complexes and Parks, Golf Course Irrigation, Golf Courses, Residential Developments, Residential Irrigation, Industrial Uses and Other Landscape Irrigation.  [62-620.630(10)(d)]

- This reuse system includes the following major users (i.e., using 0.1 MGD or more of reclaimed water):

| User Name | User Type | Capacity (MGD) | Acreage |
| --- | --- | --- | --- |
| RESCO | Industrial User | 0.571 | - |
| Cove Cay CC & Condo | Golf Course and Residential Irrigation | 0.192 | 100 |
| East Bay Country Club | Golf Course Irrigation | 0.245 | 128 |
| AIRCO GC | Golf Course Irrigation | 0.124 | 119 |
| Carillon | Other Landscape Irrigation | 0.131 | 432 |
| Totals |  | 1.263 | 779 |

[62-610.800(5)][62-620.630(10)(b)]

- New major users of reclaimed water (i.e., using 0.1 MGD or more) may be added to the reuse system using the general permit described in Rule 62-610.890, F.A.C., if the requirements in this rule are complied with.  Application for use of this general permit shall be made using Form 62-610.300(4)(a)1.  [62-610.890]

- Cross-connections to the potable water system are prohibited.  [62-610.469(7)]

- A cross-connection control program shall be implemented and/or remain in effect within the areas where reclaimed water will be provided for use.  [62-610.469(7)]

- The permittee shall conduct inspections within the reclaimed water service area to verify proper connections, to minimize illegal cross-connections, and to verify the proper use of reclaimed water.  Inspections are required when a customer first connects to the reuse distribution system.  Subsequent inspections are required as specified in the cross-connection control and inspection program.  [62-610.469(7)(h)]

- If a cross-connection between the potable and reclaimed water systems is discovered, the permittee shall:

a.	Immediately discontinue potable water and/or reclaimed water service to the affected area.

b.	If the potable water system is contaminated, clear the potable water lines.

c.	Eliminate the cross-connection.

d.	Test the affected area for other possible cross-connections.

e.	Within 24 hours, notify the Southwest District Office's domestic wastewater and drinking water programs, and the Pinellas County Health Department's drinking water program.

f.	Within 5 days of discovery of a cross-connection, submit a written report to the Department detailing: a description of the cross-connection, how the cross-connection was discovered, the exact date and time of discovery, approximate time that the cross-connection existed, the location, the cause, steps taken to eliminate the cross-connection, whether reclaimed water was consumed, and reports of possible illness, whether the drinking water system was contaminated and the steps taken to clear the drinking water system, when the cross-connection was eliminated, plan of action for testing for other possible cross-connections in the area, and an evaluation of the cross-connection control and inspection program to ensure that future cross-connections do not occur.  [62-555.350(3) and 62-555.360][62-620.610(20)]

- Maximum obtainable separation of reclaimed water lines and potable water lines shall be provided and the minimum separation distances specified in Rule 62-610.469(7), F.A.C., shall be provided.  Reuse facilities shall be color coded or marked.  Underground piping which is not manufactured of metal or concrete shall be color coded using Pantone Purple 522C using light stable colorants.  Underground metal and concrete pipe shall be color coded or marked using purple as the predominant color.  [62-610.469(7)]

- In constructing reclaimed water distribution piping, the permittee shall maintain a 75-foot setback distance from a reclaimed water transmission facility to public water supply wells.  No setback distances are required to other potable water supply wells or to any nonpotable water supply wells.  [62-610.471(3)]

- A setback distance of 75 feet shall be maintained between the edge of the wetted area and potable water supply wells, unless the utility adopts and enforces an ordinance prohibiting potable water supply wells within the reuse service area.  No setback distances are required to any nonpotable water supply well, to any surface water,  to any developed areas, or to any private swimming pools, hot tubs, spas, saunas, picnic tables, barbecue pits, or barbecue grills.  [62-610.471(1), (2), (5), and (7)]

- Reclaimed water shall not be used to fill swimming pools, hot tubs, or wading pools.  [62-610.469(4)]

- Low trajectory nozzles, or other means to minimize aerosol formation shall be used within 100 feet from outdoor public eating, drinking, or bathing facilities.  [62-610.471(6)]

- A setback distance of 100 feet shall be maintained from indoor aesthetic features using reclaimed water to adjacent indoor public eating and drinking facilities.  [62-610.471(8)]

- The public shall be notified of the use of reclaimed water.  This shall be accomplished by posting of advisory signs in areas where reuse is practiced, notes on scorecards, or other methods.  [62-610.468(2)]

- All new advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets shall bear the words “do not drink” and “no beber” along with the equivalent standard international symbol.  In addition to the words “do not drink” and “no beber,” advisory signs posted at storage ponds and decorative water features shall also bear the words “do not swim” and “no nadar” along with the equivalent standard international symbols.  Existing advisory signs and labels shall be retrofitted, modified, or replaced in order to comply with the revised wording requirements.  [62-610.468 & 62-610.469]

- The permittee shall ensure that users of reclaimed water are informed about the origin, nature, and characteristics of reclaimed water; the manner in which reclaimed water can be safely used; and limitations on the use of reclaimed water. Notification is required at the time of initial connection to the reclaimed water distribution system and annually after the reuse system is placed into operation.  A description of on-going public notification activities shall be included in the Annual Reuse Report.  [62-610.468(6)]

- Routine aquatic weed control and regular maintenance of storage pond embankments and access areas are required.  [62-610.414 & 62-610.464]

- Overflows from emergency discharge facilities on storage ponds shall be reported as an abnormal event to the Department's Southwest District Office within 24 hours of an occurrence.  The provisions of Rule 62-610.800(9), F.A.C., shall be met.  [62-610.800(9)]

V.	OPERATION AND MAINTENANCE REQUIREMENTS

1.	During the period of operation authorized by this permit, the wastewater facilities shall be operated under the supervision of an operator certified in accordance with Chapter 62-602, F.A.C.  In accordance with Chapter 62-699, F.A.C., this facility is a Category I, Class A facility and, at a minimum, operators with appropriate certification must be on the site as follows:

A Class C or higher operator 24 hours/day for 7 days/week.  The lead operator must be a Class A.

[62-620.630(3)] [62-699.310] [62-610.462]

- The lead operator shall be employed at the plant full time.  “Full time” shall mean at least 4 days per week, working a minimum of 35 hours per week, including leave time.  A certified operator shall be on-site and in charge of each required shift and for periods of required staffing time when the lead operator is not on-site.  An operator meeting the lead operator classification level of the plant shall be available during all periods of plant operation.  “Available” means able to be contacted as needed to initiate the appropriate action in a timely manner.  [62-699.311(10), (5) and (1)]

- The application to renew this permit shall include an updated capacity analysis report prepared in accordance with Rule 62-600.405, F.A.C.  [62-600.405(5)]

- The application to renew this permit shall include a detailed operation and maintenance performance report prepared in accordance with Rule 62-600.735, F.A.C.  [62-600.735(1)]

- The permittee shall maintain the following records and make them available for inspection  on the site of the permitted facility:

a.	Records of all compliance monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation and a copy of the laboratory certification showing the certification number of the laboratory, for at least three years from the date the sample or measurement was taken;

b.	Copies of all reports required by the permit for at least three years from the date the report was prepared;

c.	Records of all data, including reports and documents, used to complete the application for the permit for at least three years from the date the application was filed;

d.	Monitoring information, including a copy of the laboratory certification showing the laboratory certification number, related to the residuals use and disposal activities for the time period set forth in Chapter 62-640, F.A.C., for at least three years from the date of sampling or measurement;

e.	A copy of the current permit;

f.	A copy of the current operation and maintenance manual as required by Chapter 62-600,. F.A.C.;

g.	A copy of the facility record drawings;

h.	Copies of the licenses of the current certified operators; and

i.	Copies of  the logs and schedules showing plant operations and equipment maintenance for three years from the date of the logs or schedules.  The logs shall, at a minimum, include identification of the plant; the signature and certification number of the operator(s) and the signature of the person(s) making any entries; date and time in and out; specific operation and maintenance activities; tests performed and samples taken; and major repairs made. The logs shall be maintained on-site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed.

[62-620.350]

VI.	SCHEDULES

- The following improvement actions shall be completed according to the following schedule:

| Improvement Action |  | Completion Date |
| --- | --- | --- |
| 1 | Submit to the Department a Ground Water Monitoring Plan for Largo Central Park | Within 60 days of permit issuance. |

[62-600.735(1)]

VII.  INDUSTRIAL PRETREATMENT PROGRAM REQUIREMENTS

- The permittee shall function as the Control Authority and shall be responsible for the performance of all pretreatment program requirements contained in Chapter 62-625, F.A.C.  The permittee shall be subject to enforcement actions, penalties, and other remedies by the Department or other appropriate parties.  The permittee shall implement and enforce its Approved Pretreatment Program.  The permittee's Approved Pretreatment Program is hereby made an enforceable condition of this permit.  The Department may initiate enforcement action against an industrial user for noncompliance with applicable standards and requirements. [62-625.500]

- The permittee shall enforce the requirements promulgated under Sections 307(b), 307(c), 307(d), and 402(b) of the Act.  The permittee shall cause industrial users subject to Federal Categorical Standards to achieve compliance no later than the date specified in those requirements or, in the case of new industrial users, upon commencement of the discharge. [62-625.410]

- The permittee shall perform the pretreatment functions as required in Chapter 62-625, F.A.C., including, but not limited to, the following:

a.	Implementing the necessary legal authorities as provided in Rule 62-625.500(2)(a), F.A.C.  This includes, among other things, the authority to require compliance with applicable pretreatment standards, which includes general prohibitions listed in Rule 62-625.400(1), F.A.C., specific prohibitions in Rule 62-625.400(2), F.A.C., locally developed limits as required by Rules 62-625.400(3) and (4), F.A.C., and national categorical limits in accordance with Rule 62-625.410, F.A.C.;

b.	Implementing the programmatic functions as required under Rule 62-625.500(2)(b), F.A.C.;

c.	Providing the required funding, equipment, and personnel to implement the pretreatment program as provided in Rules 62-625.500(2), (3), and (4), F.A.C.; and

d.	Providing a written technical evaluation that local limits have been developed in accordance with Rule 62-625.400(3)(a), F.A.C.  The evaluation shall verify whether existing local limits protect the wastewater facilities, and if not, the permittee shall develop new local limits as part of the evaluation.  This evaluation shall be submitted to the Department at the address in the condition below within 180 days after permit renewal.

[62-625.400 and .500]

- As required by Rules 62-625.600(8) and (12), F.A.C., the permittee shall submit a signed copy of the annual report for pretreatment activities, including DMRs for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R, to the Department at the following address:

Florida Department of Environmental Protection

Domestic Wastewater Section, Mail Station 3540

Twin Towers Office Building

2600 Blair Stone Road

Tallahassee, Florida 32399-2400

The annual report shall contain the information required in accordance with Rule 62-625.600(8), F.A.C., except section (8)(e) as noted below, and shall describe the permittee's pretreatment activities for the reporting year.  In the event that the permittee is not in compliance with any conditions or requirements of the pretreatment program, then the permittee shall also include the reasons for noncompliance and state how and when the permittee shall comply with such conditions and requirements.

In order to comply with Rule 62-625.600(8)(e), F.A.C., the permittee shall submit annual DMRs with the analytical results of influent, effluent, and residuals for those pollutants listed on the DMRs.  For any other nonpriority pollutants which the permittee believes may be causing or contributing to interference, pass through, or adversely impacting residuals quality, the annual report shall provide a summary of all analytical results of influent, effluent, and residuals.  The annual report and DMRs are due on February 1 of each year.

[62-625.600(12)]

- Samples for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R shall be taken at the monitoring site locations described below:

| Monitoring Location Site Number | Description of Monitoring Location |
| --- | --- |
| PRT-I | At headworks prior to treatment and ahead of return activated sludge. |
| PRT-E | After declorination and prior to Outfall |
| PRT-R | From Storage Bins |

VIII.  OTHER SPECIFIC CONDITIONS

- The permittee shall apply for renewal of this permit at least 180 days before the expiration date of the permit using the appropriate forms listed in Rule 62-620.910, F.A.C., including submittal of the appropriate processing fee set forth in Rule 62-4.050, F.A.C.  The existing permit shall not expire until the Department has taken final action on the application renewal in accordance with the provisions of 62-620.335(3) and (4), F.A.C.  [62-620.335(1)-(4)]

- Florida water quality criteria and standards shall not be violated as a result of any discharge or land application of reclaimed water or residuals from this facility.  [62-620.320(9) and 62-302.500(2)(e)][62-610.850(1)(a) and (2)(a)]

- In the event that the treatment facilities or equipment no longer function as intended, are no longer safe in terms of public health and safety, or odor, noise, aerosol drift, or lighting adversely affects neighboring developed areas at the levels prohibited by Rule 62-600.400(2)(a), F.A.C., corrective action (which may include additional maintenance or modifications of the permitted facilities) shall be taken by the permittee.  Other corrective action may be required to ensure compliance with rules of the Department.  Additionally, the treatment, management, use or land application of residuals shall not cause a violation of the odor prohibition in Rule 62-296.320(2), F.A.C.  [62-600.410(8) and 62-640.400(6)]

- The deliberate introduction of stormwater in any amount into collection/transmission systems designed solely for the introduction (and conveyance) of domestic/industrial wastewater; or the deliberate introduction of stormwater into collection/transmission systems designed for the introduction or conveyance of combinations of storm and domestic/industrial wastewater in amounts which may reduce the efficiency of pollutant removal by the treatment plant is prohibited, except as provided by Rule 62-610.472, F.A.C.  [62-604.130(3)]

- Collection/transmission system overflows shall be reported to the Department in accordance with Permit Condition IX. 20.  [62-604.550]  [62-620.610(20)]

- The operating authority of a collection/transmission system and the permittee of a treatment plant are prohibited from accepting connections of wastewater discharges which have not received necessary pretreatment or which contain materials or pollutants (other than normal domestic wastewater constituents):

a.	Which may cause fire or explosion hazards; or

b.	Which may cause excessive corrosion or other deterioration of wastewater facilities due to chemical action or pH levels; or

c.	Which are solid or viscous and obstruct flow or otherwise interfere with wastewater facility operations or treatment; or

d.	Which result in the wastewater temperature at the introduction of the treatment plant exceeding 40oC or otherwise inhibiting treatment; or

e.	Which result in the presence of toxic gases, vapors, or fumes that may cause worker health or safety problems.

[62-604.130(5)]

- The treatment facility, storage ponds, rapid infiltration basins, and/or infiltration trenches shall be enclosed with a fence or otherwise provided with features to discourage the entry of animals and unauthorized persons.  [62-600.400(2)(b)]

- Screenings and grit removed from the wastewater facilities shall be collected in suitable containers and hauled to a Department approved Class I landfill or to a landfill approved by the Department for receipt/disposal of screenings and grit.  [62-701.300(1)(a)]

- The Permittee shall provide verbal notice to the Department as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The Permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department in a written report within 7 days of the sinkhole discovery.  [62-4.070(3)]

IX.	GENERAL CONDITIONS

1.	The terms, conditions, requirements, limitations and restrictions set forth in this permit are binding and enforceable pursuant to Chapter 403, Florida Statutes.  Any permit noncompliance constitutes a violation of Chapter 403, Florida Statutes, and is grounds for enforcement action, permit termination, permit revocation and reissuance, or permit revision.  [62-620.610(1)]

2.	This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviations from the approved drawings, exhibits, specifications or conditions of this permit constitutes grounds for revocation and enforcement action by the Department.  [62-620.610(2)]

3.	As provided in subsection 403.087(7), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor authorize any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit or authorization that may be required for other aspects of the total project which are not addressed in this permit.  [62-620.610(3)]

4.	This permit conveys no title to land or water, does not constitute state recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [62-620.610(4)]

5.	This permit does not relieve the permittee from liability and penalties for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source; nor does it allow the permittee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department.  The permittee shall take all reasonable steps to minimize or prevent any discharge, reuse of reclaimed water, or residuals use or disposal in violation of this permit which has a reasonable likelihood of adversely affecting human health or the environment.  It shall not be a defense for a permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this permit.  [62-620.610(5)]

6.	If the permittee wishes to continue an activity regulated by this permit after its expiration date, the permittee shall apply for and obtain a new permit.  [62-620.610(6)]

7.	The permittee shall at all times properly operate and maintain the facility and systems of treatment and control, and related appurtenances, that are installed and used by the permittee to achieve compliance with the conditions of this permit.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to maintain or achieve compliance with the conditions of the permit.  [62-620.610(7)]

8.	This permit may be modified, revoked and reissued, or terminated for cause.  The filing of a request by the permittee for a permit revision, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition.  [62-620.610(8)]

9.	The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, including an authorized representative of the Department and authorized EPA personnel, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated, to:

a.	Enter upon the permittee’s premises where a regulated facility, system, or activity is located or conducted, or where records shall be kept under the conditions of this permit;

b.	Have access to and copy any records that shall be kept under the conditions of this permit;

c.	Inspect the facilities, equipment, practices, or operations regulated or required under this permit; and

d.	Sample or monitor any substances or parameters at any location necessary to assure compliance with this permit or Department rules.

[62-620.610(9)]

10.	In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data, and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except as such use is proscribed by Section 403.111, Florida Statutes, or Rule 62-620.302, Florida Administrative Code.  Such evidence shall only be used to the extent that it is consistent with the Florida Rules of Civil Procedure and applicable evidentiary rules.  [62-620.610(10)]

11.	When requested by the Department, the permittee shall within a reasonable time provide any information required by law which is needed to determine whether there is cause for revising, revoking and reissuing, or terminating this permit, or to determine compliance with the permit.  The permittee shall also provide to the Department upon request copies of records required by this permit to be kept.  If the permittee becomes aware of relevant facts that were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be promptly submitted or corrections promptly reported to the Department.  [62-620.610(11)]

12.	Unless specifically stated otherwise in Department rules, the permittee, in accepting this permit, agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.  A reasonable time for compliance with a new or amended surface water quality standard, other than those standards addressed in Rule 62-302.500, F.A.C., shall include a reasonable time to obtain or be denied a mixing zone for the new or amended standard.  [62-620.610(12)]

13.	The permittee, in accepting this permit, agrees to pay the applicable regulatory program and surveillance fee in accordance with Rule 62-4.052, F.A.C.  [62-620.610(13)]

14.	This permit is transferable only upon Department approval in accordance with Rule 62-620.340, F.A.C.  The permittee shall be liable for any noncompliance of the permitted activity until the transfer is approved by the Department.  [62-620.610(14)]

15.	The permittee shall give the Department written notice at least 60 days before inactivation or abandonment of a wastewater facility and shall specify what steps will be taken to safeguard public health and safety during and following inactivation or abandonment.  [62-620.610(15)]

16.	The permittee shall apply for a revision to the Department permit in accordance with Rules 62-620.300 and the Department of Environmental Protection Guide to Wastewater Permitting at least 90 days before construction of any planned substantial modifications to the permitted facility is to commence or with Rule 62-620.325(2) for minor modifications to the permitted facility.  A revised permit shall be obtained before construction begins except as provided in Rule 62-620.300, F.A.C.  [62-620.610(16)]

17.	The permittee shall give advance notice to the Department of any planned changes in the permitted facility or activity which may result in noncompliance with permit requirements.  The permittee shall be responsible for any and all damages which may result from the changes and may be subject to enforcement action by the Department for penalties or revocation of this permit.  The notice shall include the following information:

a.	A description of the anticipated noncompliance;

b.	The period of the anticipated noncompliance, including dates and times; and

c.	Steps being taken to prevent future occurrence of the noncompliance.

[62-620.610(17)]

18.	Sampling and monitoring data shall be collected and analyzed in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.

a.	Monitoring results shall be reported at the intervals specified elsewhere in this permit and shall be reported on a Discharge Monitoring Report (DMR), DEP Form 62-620.910(10), or as specified elsewhere in the permit.

b.	If the permittee monitors any contaminant more frequently than required by the permit, using Department approved test procedures, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the DMR.

c.	Calculations for all limitations which require averaging of measurements shall use an arithmetic mean unless otherwise specified in this permit.

d.	Except as specifically provided in Rule 62-160.300, F.A.C., any laboratory test required by this permit shall be performed by a laboratory that has been certified by the Department of Health Environmental Laboratory Certification Program (DOH ELCP).  Such certification shall be for the matrix, test method and analyte(s) being measured to comply with this permit.  For domestic wastewater facilities, testing for parameters listed in Rule 62-160.300(4), F.A.C., shall be conducted under the direction of a certified operator.

e.	Field activities including on-site tests and sample collection shall follow the applicable standard operating procedures described in DEP-SOP-001/01 adopted by reference in Chapter 62-160, F.A.C.

f.	Alternate field procedures and laboratory methods may be used where they have been approved in accordance with Rules 62-160.220 and 62-160.330, F.A.C.

[62-620.610(18)]

19.	Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule detailed elsewhere in this permit shall be submitted no later than 14 days following each schedule date.  [62-620.610(19)]

20.	The permittee shall report to the Department any noncompliance which may endanger health or the environment.  Any information shall be provided orally within 24 hours from the time the permittee becomes aware of the circumstances.  A written submission shall also be provided within five days of the time the permittee becomes aware of the circumstances.  The written submission shall contain:  a description of the noncompliance and its cause; the period of noncompliance including exact dates and time, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.

a.	The following shall be included as information which must be reported within 24 hours under this condition:

1.	Any unanticipated bypass which causes any reclaimed water or effluent to exceed any permit limitation or results in an unpermitted discharge,

2.	Any upset which causes any reclaimed water or the effluent to exceed any limitation in the permit,

3.	Violation of a maximum daily discharge limitation for any of the pollutants specifically listed in the permit for such notice, and

4.	Any unauthorized discharge to surface or ground waters.

b.	Oral reports as required by this subsection shall be provided as follows:

1.	For unauthorized releases or spills of treated or untreated wastewater reported pursuant to subparagraph a.4 that are in excess of 1,000 gallons per incident, or where information indicates that public health or the environment will be endangered, oral reports shall be provided to the Department by calling the STATE WARNING POINT TOLL FREE NUMBER (800) 320-0519, as soon as practical, but no later than 24 hours from the time the permittee becomes aware of the discharge. The permittee, to the extent known, shall provide the following information to the State Warning Point:

- Name, address, and telephone number of person reporting;

- Name, address, and telephone number of permittee or responsible person for the discharge;

- Date and time of the discharge and status of discharge (ongoing or ceased);

- Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater);

- Estimated amount of the discharge;

- Location or address of the discharge;

- Source and cause of the discharge;

- Whether the discharge was contained on-site, and cleanup actions taken to date;

- Description of area affected by the discharge, including name of water body affected, if any; and

- Other persons or agencies contacted.

2.	Oral reports, not otherwise required to be provided pursuant to subparagraph b.1 above,  shall be provided to the Department within 24 hours from the time the permittee becomes aware of the circumstances.

c.	If the oral report has been received within 24 hours, the noncompliance has been corrected, and the noncompliance did not endanger health or the environment, the Department shall waive the written report.

[62-620.610(20)]

21.	The permittee shall report all instances of noncompliance not reported under Permit Conditions IX. 17., 18. and 19. of this permit at the time monitoring reports are submitted.  This report shall contain the same information required by Permit Condition IX. 20 of this permit.  [62-620.610(21)]

22.	Bypass Provisions.

a.	Bypass is prohibited, and the Department may take enforcement action against a permittee for bypass, unless the permittee affirmatively demonstrates that:

1.	Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage; and

2.	There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

3.	The permittee submitted notices as required under Permit Condition IX. 22. b. of this permit.

b.	If the permittee knows in advance of the need for a bypass, it shall submit prior notice to the Department, if possible at least 10 days before the date of the bypass.  The permittee shall submit notice of an unanticipated bypass within 24 hours of learning about the bypass as required in Permit Condition IX. 20. of this permit.  A notice shall include a description of the bypass and its cause; the period of the bypass, including exact dates and times; if the bypass has not been corrected, the anticipated time it is expected to continue; and the steps taken or planned to reduce, eliminate, and prevent  recurrence of the bypass.

c.	The Department shall approve an anticipated bypass, after considering its adverse effect, if the permittee demonstrates that it will meet the three conditions listed in Permit Condition IX. 22. a. 1. through 3. of this permit.

d.	A permittee may allow any bypass to occur which does not cause reclaimed water or effluent limitations to be exceeded if it is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of Permit Condition IX. 22. a. through c. of this permit.

[62-620.610(22)]

23.	Upset Provisions

a.	A permittee who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed contemporaneous operating logs, or other relevant evidence that:

1.	An upset occurred and that the permittee can identify the cause(s) of the upset;

2.	The permitted facility was at the time being properly operated;

3.	The permittee submitted notice of the upset as required in Permit Condition IX. 20. of this permit; and

4.	The permittee complied with any remedial measures required under Permit Condition IX. 5. of this permit.

b.	In any enforcement proceeding, the burden of proof for establishing the occurrence of an upset rests with the permittee.

c.	Before an enforcement proceeding is instituted, no representation made during the Department review of a claim that noncompliance was caused by an upset is final agency action subject to judicial review.

[62-620.610(23)]

Executed in Hillsborough County, Florida.

STATE OF FLORIDA DEPARTMENT OF                         ENVIRONMENTAL PROTECTION

____________________________________

Jeffry S. Greenwell, P.E.

Water Facilities Administrator

Southwest District

13051 N. Telecom Parkway

Temple Terrace, FL  33637-0926