FACT SHEET

FOR

STATE OF FLORIDA

DOMESTIC WASTEWATER FACILITY PERMIT

| PERMIT NUMBER: | FL0141399 |
| --- | --- |
| PA FILE NUMBER: | FL0141399-022-DW1P |
| FACILITY NAME: | Collier County North Regional WWTP |
| FACILITY LOCATION: | Naples Collier County |
| NAME OF PERMITTEE: | Collier County Water-Sewage District |
| PERMIT WRITER: | Brandon Ivey |

1.	SYNOPSIS OF APPLICATION

a.	Chronology of Application

|  | Application Date: | August 17, 2007 |
| --- | --- | --- |
|  | Additional Information: | RFI #1 – September 14, 2007 RFI #2 – November 8, 2007 |
|  | Draft Public Notice Date: | March 12, 2008 |
|  | Public Meeting Notice Date: | May, 13, 2008 |
|  | Public Meeting Date: | June 12, 2008 |
|  | Intent Public Notice Date: | August 8, 2008 |

b.	Type of Facility

Domestic Wastewater Treatment Plant

Publicly-owned treatment works

Standard Industrial Classification Code: 4952

c.	Facility Capacity

|  | Existing Design Capacity: | 24.1 | MGD | MADF |
| --- | --- | --- | --- | --- |
|  | Proposed Increase in Design Capacity: | 6.5 | MGD | MADF |
|  | Proposed Total Design Capacity: | 30.6 | MGD | MADF |

|  | Existing Permitted Capacity: | 24.1 | MGD | MADF |
| --- | --- | --- | --- | --- |
|  | Proposed Increase in Permitted Capacity: | 6.5 | MGD | MADF |
|  | Proposed Total Permitted Capacity: | 30.6 | MGD | MADF |

d.	Description of Effluent or Reclaimed Water Discharges (as reported by applicant)

See attached map(s) for the location(s) of effluent disposal and land application sites.

This section is not applicable. There are no surface water discharges.

2.	BASIS FOR EFFLUENT AND RECLAIMED WATER LIMITS AND MONITORING REQUIREMENTS (INCLUDING EFFLUENT MONITORING REQUIREMENTS)

The following table provides the basis for Part I. A. provisions.

Outfall D-001 and D-002:

Vineyards Golf Course Lakes

D-001 is for the existing stormwater outfall numbers, STM-01 North and STM-02 South which are associated with the Vineyards golf course lakes being used to store public access reuse water that has outfalls to state waters. Stormwater outfalls intermittently discharge to the D-2 Canal with eventual discharge to the Naples Bay via the Gordon River. The approximate locations of STM-01 North is Latitude 26' 14' 00" N, Longitude 81o 43' 19" W and STM-02 South is Latitude 26 o 12' 58" N, Longitude 81o 43' 13" W, which discharge to state surface waters.

Discharge of reclaimed water to the lakes listed in the table below at Vineyards Golf Course Lakes stormwater storage lake system D-001 shall only occur when the elevation of the water in each lake is less than the corresponding control elevation listed in the table below.  A list of all days during a month on which discharges from each lake to the receiving water body occurred shall be attached to the DMR form.  For each day on which discharge occurred, the approximate number of hours of discharge shall be noted.  [62-610.830(1) and (3)]

| Monitoring Location Site Number | Name of Storage Lake/Description of Monitoring Location | Control Elevation (ft. M.S.L.) | Receiving Water Body |
| --- | --- | --- | --- |
| STM-01 | North Vineyards Golf Course Outfall | 9.2 | D-2 Canal to Gordon River to Naples Bay |
| STM-02 | South Vineyards Golf Course Outfall | 9.2 | D-2 Canal to Gordon River to Naples Bay |

Bermuda Greens Condominiums

D-002 is for existing stormwater outfall number STM-03 associated with a stormwater lake at the Bermuda Greens Condominiums that has a preserve mound of vegetation requiring the control elevation to be maintained at eight (8) feet NGVD. The stormwater outfall intermittently discharges to a manmade canal that flows to the Palm River Canal that discharges to the Cocohatchee River. The approximate location of STM-03 is Latitude 26 o 17' 30'N and Longitude 81 o 47' 00" W.

Discharge of reclaimed water to the lakes listed in the table below at the Bermuda Greens development shall only occur when the elevation of the water in each lake is less than the corresponding control elevation listed in the table below.  A list of all days during a month on which discharges from each lake to the receiving water body occurred shall be attached to the DMR form.  For each day on which discharge occurred, the approximate number of hours of discharge shall be noted.  [62-610.830(1) and (3)]

| Monitoring Location Site Number | Name of Storage Lake/Description of Monitoring Location | Control Elevation (ft. M.S.L.) | Receiving Water Body |
| --- | --- | --- | --- |
| STM-03 | Bermuda Greens Outfall | 7.5 | Unnamed Canal to Palm River to Cocohatchee River |

UIC System U-001 and U-002 (Class I wells to Class G-IV waters):

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (MGD) | 17.0 MGD | Monthly Aveage | 62-600.400(3)(b) FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | 20.0 30.0 45.0 60.0 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-600.540(1) & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.c. FAC 62-600.740(1)(b)1.d. FAC |
| Solids, Total Suspended (MG/L) | 5.0 | Single Sample Max. | 62-600.440(5)(f)3. FAC |
| pH (SU) | 6.0 to 8.5 | Minimum and Maximum | 62-600.445 FAC |
| Coliform, Fecal (#/100ML) | 25 | Single Sample Max. | 62-600.440(5)(f)2. FAC |
| Coliform, Fecal, % less than detection (PERCENT) | 75 | Monthly Average | 62-600.440(5)(f)1. FAC |
| Chlorine, Total Residual (MG/L) | 1.0 | Single Sample Min. | 62-600.440(5)(b) or (c) FAC |

UIC System U-003 and U-004 (Class I wells to Class G-IV waters):

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (MGD) | 4.0 MGD | Annual Average | 62-600.400(3)(b) FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | 20.0 30.0 45.0 60.0 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-600.540(1) & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.c. FAC 62-600.740(1)(b)1.d. FAC |
| Solids, Total Suspended (MG/L) | 20 30 45 60 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-600.540(1) & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.c. FAC 62-600.740(1)(b)1.d. FAC |
| pH (SU) | 6.0 to 8.5 | Minimum and Maximum | 62-600.445 FAC |
| Chlorine, Total Residual (MG/L) | 0.5 | Single Sample Min. | 62-600.440(5)(b) or (c) FAC |
| Coliform, Fecal (#/100ML) | 25.0 | Single Sample Max. | 62-600.440(5)(f)2. FAC |
| Coliform, Fecal, % less than detection (PERCENT) | 75 | Monthly Average | 62-600.440(5)(f)1. FAC |

UIC System U-005 (Class V wells to Class G-II waters):

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (to ASR well) (MGD) | Report Report | Annual Average Monthly Average | 62-600.400(3)(b) FAC 62-600.400(3)(b) FAC |
| Coliform, Total (#/100ML) | 1 + reading 4 | Monthly Total Single Sample Max. | 62-550.310(3) FAC 62-520.420(1) FAC |
| Conductance, Specific (UMHO/CM) | Report Report | Monthly Average Single Sample Max. | 62-610.466(12)(c)1. FAC 62-610.466(12)(c)1. FAC |
| Total Residual Chlorine (For Disinfection) (MG/L) | Report | Minimum | 62-610.466(9)(b)1. & 62-600.440(5)(b) FAC |
| Primary Drinking Water Standards | - | Maximum | 62-610.466(9)(b)1. & 62-550.310 FAC |
| Chloride (as Cl) (MG/L) | Report Report | Monthly Average Single Sample Max. | 62-610.466(12)(c)1. FAC 62-610.466(12)(c)1. FAC |
| Solids, Total Dissolved (TDS) (MG/L) | Report Report | Monthly Average Single Sample Max. | 62-610.466(12)(c)1. FAC 62-610.466(12)(c)1. FAC |
| pH (SU) | 6.0 to 8.5 | Minimum and Maximum | 62-610.466(9)(b)1. FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | 20.0 30.0 45.0 60.0 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-610.460 & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.d. FAC |
| Solids, Total Suspended (MG/L) | 5.0 | Single Sample Max. | 62-610.460(1) & 62-600.440(5)(f)3. FAC |
| Chlorine, Total Residual (MG/L) | 1.0 | Single Sample Min. | 62-600.440(5)(b), 62-610.460(2), & 62-610.463(2) FAC |
| Turbidity (NTU) | Report | Single Sample Max. | See condition I.B.7 of previous permit |
| Aluminum, Total Recoverable (MG/L) | 0.2 | Single Sample Max. | 62-550.320(1) FAC |
| Chloride (as Cl) (MG/L) | 250 | Single Sample Max. | 62-550.320(1) FAC |
| Copper, Total Recoverable (UG/L) | 1.0 | Single Sample Max. | 62-550.320(1) FAC |
| Fluoride, Total (as F) (MG/L) | 2.0 | Single Sample Max. | 62-550.320(1) FAC & 62-550.320(2) FAC |
| Iron, Total Recoverable (MG/L) | 0.3 | Single Sample Max. | 62-550.320(1) FAC |
| Manganese, Total Recoverable (MG/L) | 0.05 | Single Sample Max. | 62-550.320(1) FAC |
| Silver, Total Recoverable (UG/L) | 0.1 | Single Sample Max. | 62-550.320(1) FAC |
| Sulfate, Total (MG/L) | 250 | Single Sample Max. | 62-550.320(1) FAC |
| Zinc, Total Recoverable (UG/L) | 5.0 | Single Sample Max. | 62-550.320(1) FAC |
| Foaming Agents (MG/L) | 0.5 | Single Sample Max. | 62-550.320(1) FAC |

The following table provides the basis for Part I. B. provisions.

Land Application System R-001 (slow-rate public access):

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (MGD) | 25.34 | Annual Average | 62-600.400(3)(b) FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | 20.0 30.0 45.0 60.0 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-610.460 & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.c. FAC 62-600.740(1)(b)1.d. FAC |
| Solids, Total Suspended (MG/L) | 5.0 | Single Sample Max. | 62-610.460(1) & 62-600.440(5)(f)3. FAC |
| pH (SU) | 6.0 to 8.5 | Minimum and Maximum | 62-600.445 FAC |
| Coliform, Fecal (#/100ML) | 25 | Single Sample Max. | 62-610.460 & 62-600.440(5)(f)2. FAC |
| Coliform, Fecal, % less than detection (PERCENT) | 75 | Monthly Average | 62-600.440(5)(f)1. FAC |
| Total Residual Chlorine (For Disinfection) (MG/L) | 1.0 | Minimum | 62-600.440(5(b), 62-610.460(2), & 62-610.463(2) FAC |
| Turbidity (NTU) | Report | Single Sample Max. | 62-610.463(2) FAC |
| Giardia (CYSTS/100 L) | Report | Single Sample Max. | 62-610.463(4) FAC |
| Cryptosporidium (OOCYSTS/100 L) | Report | Single Sample Max. | 62-600.463(4) FAC |

| Bulk Users of Reclaimed Water |  |  |  |
| --- | --- | --- | --- |
| Current Reclaimed Water Users |  |  |  |
| User Name | User Type | Capacity (MGD) | Acreage |
| Audubon Joint Venture | Golf Course Irrigation/Residential | 0.822 | 203.0 |
| Autumn Woods | Other Irrigation/Residential | 0.230 | 60.0 |
| Beachwalk Residents Association | Other Irrigation | 0.110 | 25.0 |
| Bermuda Green | Other Irrigation | 0.019 | 15.0 |
| Calusa Bay | Other Irrigation | 0.100 | 20.0 |
| Charleston Square | Other Irrigation | 0.010 | 15.0 |
| Collier Reserve – CDC | Golf Course Irrigation | 0.400 | 70.0 |
| Imperial Golf Club, Inc. | Golf Course Irrigation | 1.010 | 260.0 |
| North Naples Regional Park | Other Irrigation | 0.349 | 90.0 |
| Palm River Country Club (La Playa) | Golf Course Irrigation | 0.700 | 75.0 |
| The Club at Pelican Bay | Other Irrigation/Golf course | 0.500 | 100.0 |
| Pelican Bay | Other Irrigation/Residential | 3.700 | 674.0 |
| Pelican Marsh | Golf Course & Residential Irrigation | 3.880 | 1000.0 |
| Tarpon Cove | Other Irrigation | 0.146 | 38.0 |
| Collier County DOT | Other Irrigation | 0.750 | 170.0 |
| Veteran’s Park (County) | Other Irrigation | 0.040 | 10.0 |
| Vineyards Park | Other Irrigation | 0.099 | 25.0 |
| Vineyards Utility, Inc. | Golf Course Irrigation | 3.020 | 778.0 |
| Total Existing Users |  | 15.885 | 3628 |
| Future Reclaimed Water Users |  |  |  |
| User Name | User Type | Capacity (MGD) | Acreage |
| Aston | Residential Irrigation | 0.06 | 15.0 |  |
| Carlton Lakes | Residential Irrigation | 0.950 | 245.0 |  |
| Cocohatchee Bay | Golf Course Irrigation | 0.582 | 150.0 |  |
| Collier County Public Schools | Other Irrigation | 0.686 | 126.0 |  |
| Collier Reserve Association Inc. | Golf Course Irrigation | 0.648 | 168.0 |  |
| Grey Oaks | Golf Course Irrigation | 1.746 | 450.0 |  |
| Island Walk | Other Irrigation | 0.970 | 250.0 |  |
| Village Walk | Golf Course Irrigation | 0.388 | 100.0 |  |
| Kensington Golf Club | Golf Course Irrigation | 0.788 | 201.0 |  |
| Longshore Lakes | Other Irrigation | 0.892 | 230.0 |  |
| Olde Cypress Golf Club | Golf Course Irrigation | 0.931 | 240.0 |  |
| The Strand | Golf Course Irrigation | 0.970 | 250.0 |  |
| Quail Village | Golf Course Irrigation | 0.582 | 150.0 |  |
| Quail Creek Country Club | Golf Course Irrigation | 0.931 | 240.0 |  |
| Quail West | Golf Course Irrigation | 2.199 | 567.0 |  |
| St. Croix | Residential Irrigation | 0.06 | 15.0 |  |
| Sterling Oaks | Golf Course Irrigation | 1.071 | 276.0 |  |
| Stonebridge | Golf Course Irrigation | 0.504 | 130.0 |  |
| Wilkshire | Other Irrigation | 0.194 | 50.0 |  |
| Total Future Users |  | 15.152 | 3853 |
| Total Current and Future User Capacity |  | 31.037 | 7481 |

The public access reuse system (R-001) is provided with an existing supplemental water supply system.  A Minor modification (FL0141399-009) includes six existing irrigation wells (water table aquifer production wells).  The subject well field is located along Naples – Immokalee Road and adjacent to a surface water canal.

The applicant shall provide an affirmative demonstration that the quality of the resulting mixture of reclaimed water and ground water will be acceptable for the permitted uses of the reclaimed water within the reclaimed water distribution system.  This shall include an evaluation of the factors contained in Rule 62-610.472(3)(a) 2., F.A.C.  This include an analysis of the ground water source for all of the parameters included in the ground water source for all of the parameters included in the ground water quality standards listed in Chapter 62-520, F.A.C.

Monitoring of the ground water supply shall be conducted quarterly for fecal coliforms, unless additional monitoring is required by Rule 62-610.472(4)(b), F.A.C.

Land Application System R-001 (slow-rate public access, ASR System):

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (from ASR system) (MGD) | Report Report | Annual Average Monthly Average | 62-600.400(3)(b) FAC 62-600.400(3)(b) FAC |
| Flow(from ASR well to reject) (MGD) | Report Report | Annual Average Monthly Average | 62-600.400(3)(b) FAC 62-600.400(3)(b) & 62-610.810(5) FAC & 62-610.466(17) FAC |
| Percent Capacity, (TMADF/Permitted Capacity) x 100 (PERCENT) | Report | Annual Average | 62-610.466(17) FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | 20.0 30.0 45.0 60.0 | Annual Average Monthly Average Weekly Average Single Sample Max. | 62-610.460 & 62-600.740(1)(b)1.a. FAC 62-600.740(1)(b)1.b. FAC 62-600.740(1)(b)1.c. FAC 62-600.740(1)(b)1.d. FAC |
| Solids, Total Suspended (MG/L) | 5.0 | Single Sample Max. | 62-610.460(1) & 62-600.440(5)(f)3. FAC |
| Coliform, Fecal (from ASR system) (#/100ML) | 25 | Single Sample Max. | 62-610.460 & 62-600.440(5)(f)2. FAC |
| Coliform, Fecal, % less than detection (from ASR system) (PERCENT) | 75 | Monthly Average | 62-600.440(5)(f)1. FAC |
| Conductance, Specific (from ASR system) (UMHO/CM) | Report Report | Monthly Average Single Sample Max. | 62-610.466(12)(c)1. FAC 62-610.466(12)(c)1. FAC |
| Total Residual Chlorine (For Disinfection) (MG/L) | Report | Minimum | 62-600.440(5(b), 62-610.460(2), & 62-610.463(2) FAC |
| Ultraviolet Light Transmittance (PERCENT) | Report | Single Sample Min. | 62-610.463(1) FAC, 62-610.463(2) FAC |
| Chloride (as Cl) (from ASR well) (MG/L) | Report | Weekly Average | 62-610.466(12)(c)1. FAC |
| Solids, Total Dissolved (TDS) (MG/L) | Report | Weekly Average | 62-610.466(12)(c)1. FAC |

The following table provides the basis for Part I. C. provisions.

Other Limitations and Monitoring Requirements:

| Parameter | Limit | Basis | Rationale |
| --- | --- | --- | --- |
| Flow (MGD) | 30.6 | Monthly Average | 62-600.400(3)(b)FAC |
| Flow (MGD) | Report | Monthly Average | 62-600.400(3)(b)FAC |
| Flow (MGD) | Report | Monthly Average | 62-600.400(3)(b)FAC |
| Flow (MGD) | Report | Monthly Average | 62-600.400(3)(b)FAC |
| Percent Capacity, (TMADF/Permitted Capacity) x 100 (PERCENT) | Report | Monthly Average | 62-600.405(4) FAC |
| BOD, Carbonaceous 5 day, 20C (MG/L) | Report | Monthly Average | 62-601.300(1)FAC |
| Solids, Total Suspended (MG/L) | Report | Monthly Average | 62-601.300(1)FAC |
| Nitrogen, Total (MG/L) | 12.0 | Single Sample Max. | 62-610.510(1) FAC |
| Monitoring Frequency and Sample Type | - | All Parameters | 62-601 FAC & 62-699 FAC and/or BPJ of permit writer |
| Sampling Location | - | All Parameters | 62-601, 62-610.412, 62-610.463(1), 62-610.568, 62-610.613 FAC and/or BPJ of permit writer |

3.	RESIDUALS MANAGEMENT

The method of residuals use or disposal by this facility is disposal in a Class I or II solid waste landfill.

4.	GROUND WATER MONITORING REQUIREMENTS

Ground water monitoring requirements have been established in accordance with Rules 62-601 and 62-522, F.A.C.

5.	SCHEDULES FOR IMPROVEMENT ACTIONS, CONSTRUCTION, AND ENGINEERING STUDIES

The following construction schedule for the facilities shall be followed, unless a minor permit revision is issued to amend the schedule:

|  | Implementation Step |  | Completion Date |
| --- | --- | --- | --- |
|  | 1 | Submit the Completion of Construction | April 30, 2011 |
|  | 2 | Submit the Notification of Availability of Record Drawings | October 31, 2011 |

6.	INDUSTRIAL PRETREATMENT REQUIREMENTS

An industrial pretreatment program in accordance with Chapter 403, F. S., and Chapter 62-625, F.A.C has been added to the permit.

7.	NEW OR EXPANDED DISCHARGES TO SURFACE WATERS; ANTIDEGRADATION REQUIREMENTS

This section is not applicable to this facility.

8.	APPLICABLE RULES

The following were used as the basis of the permit limitations/conditions:

a. FAC refers to various portions of the Florida Administrative Code. The effective dates of FAC Rule Chapters cited in the table are as follows: Chapter Effective Date 62-4 05-01-03 62-160 04-09-02 62-302 05-15-02 62-520 12-09-96 62-522 08-27-01 62-550 05-28-03 62-600 12-24-96 62-601 12-24-96 62-602 02-06-02 62-610 03-09-07 62-620 08-25-03 62-625 01-08-97 62-640 03-30-98 62-650 12-26-96 62-699 07-05-01 b. FS refers to various portions of the Florida Statutes c. CFR refers to various portions of the Code of Federal Regulations, Title 40 d. BPJ refers to Best Professional Judgment

9.	DEPARTMENT CONTACT

Additional information concerning the permit may be obtained during normal business hours from:

Brandon Ivey

Engineering Specialist

Department's South District Office

Department of Environmental Protection,

P.O. Box 2549

Ft. Myers, FL, 33902 - 2549

Telephone Number: (239) 332-6975

Fax Number: (239) 332-6969

10.	THE ADMINISTRATIVE RECORD

The administrative record including application, draft permit, fact sheet, public notice (after release), comments received and additional information is available for public inspection during normal business hours at the location specified in item 13.