2000-03-31 | BOD, Carbonaceous 5 day, 20C | 3.2 | MG/L
2000-03-31 | BOD, Carbonaceous 5 day, 20C | 2.2 | MG/L
2000-03-31 | Solids, Total Suspended | 6.6 | MG/L
2000-03-31 | Solids, Total Suspended | 10 | MG/L
2000-03-31 | Solids, Total Suspended | 6.9 | MG/L
2000-03-31 | pH | 6.9 | SU
2000-03-31 | pH | 7.4 | SU
2000-03-31 | Nitrogen, Total | 320 | LBS/DAY
2000-03-31 | Nitrogen, Total | 7.95 | MG/L
2000-03-31 | Phosphorus, Total (as P) | 0.14 | MG/L
2000-03-31 | Phosphorus, Total (as P) | 6 | LBS/DAY
2000-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
2000-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 100 | #/100ML
2000-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
2000-03-31 | Oxygen, Dissolved (DO) | 6.2 | MG/L
2000-03-31 | Oxygen, Dissolved (DO) | 6.2 | MG/L
2000-03-31 | Chlorine, Total Residual | anc | MG/L
2000-03-31 | Chlorine, Total Residual | 0.001 | MG/L
2000-03-31 | Solids, Total Suspended | 2.9 | MG/L
2000-03-31 | Chlorine, Total Residual | 1.5 | MG/L
2000-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <2.0 | #/100ML
2000-02-29 | Flow, Wwtp, Monthly Average | 5.67 | MGD
2000-02-29 | Flow, Wwtp, Monthly Average | 6.26 | MGD
2000-02-29 | BOD, Carbonaceous 5 day, 20C | 243 | MG/L
2000-02-29 | BOD, Carbonaceous 5 day, 20C | 648 | MG/L
2000-02-29 | Solids, Total Suspended | 235 | MG/L
2000-02-29 | Solids, Total Suspended | 430 | MG/L
2000-02-29 | BOD, Carbonaceous 5 day, 20C | 2.2 | MG/L
2000-02-29 | BOD, Carbonaceous 5 day, 20C | 3.9 | MG/L
2000-02-29 | BOD, Carbonaceous 5 day, 20C | 5.8 | MG/L
2000-02-29 | Solids, Total Suspended | 13.5 | MG/L
2000-02-29 | Solids, Total Suspended | 7.2 | MG/L
2000-02-29 | Solids, Total Suspended | 7.2 | MG/L
2000-02-29 | pH | 7.4 | SU
2000-02-29 | pH | 6.7 | SU
2000-02-29 | Nitrogen, Total | 5.76 | MG/L
2000-02-29 | Nitrogen, Total | 234 | LBS/DAY
2000-02-29 | Phosphorus, Total (as P) | 6 | LBS/DAY
2000-02-29 | Phosphorus, Total (as P) | 0.15 | MG/L
2000-02-29 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 17 | #/100ML
2000-02-29 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 4 | #/100ML
2000-02-29 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
2000-02-29 | Oxygen, Dissolved (DO) | 6.1 | MG/L
2000-02-29 | Oxygen, Dissolved (DO) | 6.1 | MG/L
2000-02-29 | Chlorine, Total Residual | 0.8 | MG/L
2000-02-29 | Chlorine, Total Residual | <0.001 | MG/L
2000-02-29 | Solids, Total Suspended | 3.9 | MG/L
2000-02-29 | Chlorine, Total Residual | 1.5 | MG/L
2000-02-29 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 7 | #/100ML
2000-01-31 | Flow, Wwtp, Monthly Average | 6.58 | MGD
2000-01-31 | Flow, Wwtp, Monthly Average | 5.92 | MGD
2000-01-31 | BOD, Carbonaceous 5 day, 20C | 241 | MG/L
2000-01-31 | BOD, Carbonaceous 5 day, 20C | 156 | MG/L
2000-01-31 | Solids, Total Suspended | 204 | MG/L
2000-01-31 | Solids, Total Suspended | 145 | MG/L
2000-01-31 | BOD, Carbonaceous 5 day, 20C | 6.6 | MG/L
2000-01-31 | BOD, Carbonaceous 5 day, 20C | 2.1 | MG/L
2000-01-31 | BOD, Carbonaceous 5 day, 20C | 2.9 | MG/L
2000-01-31 | Solids, Total Suspended | 7.1 | MG/L
2000-01-31 | Solids, Total Suspended | 28.1 | MG/L
2000-01-31 | Solids, Total Suspended | 7.8 | MG/L
2000-01-31 | pH | 6.8 | SU
2000-01-31 | pH | 7.2 | SU
2000-01-31 | Nitrogen, Total | 83 | LBS/DAY
2000-01-31 | Nitrogen, Total | 1.9 | MG/L
2000-01-31 | Phosphorus, Total (as P) | 0.16 | MG/L
2000-01-31 | Phosphorus, Total (as P) | 7 | LBS/DAY
2000-01-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
2000-01-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 2 | #/100ML
2000-01-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 4 | #/100ML
2000-01-31 | Oxygen, Dissolved (DO) | 6 | MG/L
2000-01-31 | Oxygen, Dissolved (DO) | 6 | MG/L
2000-01-31 | Chlorine, Total Residual | 0.8 | MG/L
2000-01-31 | Chlorine, Total Residual | <0.001 | MG/L
2000-01-31 | Solids, Total Suspended | 4.8 | MG/L
2000-01-31 | Chlorine, Total Residual | 1.5 | MG/L
2000-01-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 2 | #/100ML
1999-12-31 | Flow, Wwtp, Monthly Average | 6.14 | MGD
1999-12-31 | Flow, Wwtp, Monthly Average | 6.62 | MGD
1999-12-31 | BOD, Carbonaceous 5 day, 20C | 155 | MG/L
1999-12-31 | BOD, Carbonaceous 5 day, 20C | 2.64 | MG/L
1999-12-31 | Solids, Total Suspended | 139 | MG/L
1999-12-31 | Solids, Total Suspended | 260 | MG/L
1999-12-31 | BOD, Carbonaceous 5 day, 20C | 5.1 | MG/L
1999-12-31 | BOD, Carbonaceous 5 day, 20C | 2.2 | MG/L
1999-12-31 | BOD, Carbonaceous 5 day, 20C | 2.7 | MG/L
1999-12-31 | Solids, Total Suspended | 7.3 | MG/L
1999-12-31 | Solids, Total Suspended | 17.4 | MG/L
1999-12-31 | Solids, Total Suspended | 7.4 | MG/L
1999-12-31 | pH | 7.2 | SU
1999-12-31 | pH | 6.8 | SU
1999-12-31 | Nitrogen, Total | 1.92 | MG/L
1999-12-31 | Nitrogen, Total | 91 | LBS/DAY
1999-12-31 | Phosphorus, Total (as P) | 0.09 | MG/L
1999-12-31 | Phosphorus, Total (as P) | 4 | LBS/DAY
1999-12-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-12-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 1 | #/100ML
1999-12-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 12 | #/100ML
1999-12-31 | Oxygen, Dissolved (DO) | 5.6 | MG/L
1999-12-31 | Oxygen, Dissolved (DO) | 5.6 | MG/L
1999-12-31 | Chlorine, Total Residual | 0.5 | MG/L
1999-12-31 | Chlorine, Total Residual | <0.01 | MG/L
1999-12-31 | Solids, Total Suspended | 1.6 | MG/L
1999-12-31 | Chlorine, Total Residual | 1.5 | MG/L
1999-12-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 4 | #/100ML
1999-11-30 | Flow, Wwtp, Monthly Average | 7.98 | MGD
1999-11-30 | Flow, Wwtp, Monthly Average | 8.41 | MGD
1999-11-30 | BOD, Carbonaceous 5 day, 20C | 363 | MG/L
1999-11-30 | BOD, Carbonaceous 5 day, 20C | 157 | MG/L
1999-11-30 | Solids, Total Suspended | 181 | MG/L
1999-11-30 | Solids, Total Suspended | 384 | MG/L
1999-11-30 | BOD, Carbonaceous 5 day, 20C | 2.8 | MG/L
1999-11-30 | BOD, Carbonaceous 5 day, 20C | 2.1 | MG/L
1999-11-30 | BOD, Carbonaceous 5 day, 20C | 2.1 | MG/L
1999-11-30 | Solids, Total Suspended | 12.9 | MG/L
1999-11-30 | Solids, Total Suspended | 7.1 | MG/L
1999-11-30 | Solids, Total Suspended | 6 | MG/L
1999-11-30 | pH | 7.3 | SU
1999-11-30 | pH | 6.8 | SU
1999-11-30 | Nitrogen, Total | 1.33 | MG/L
1999-11-30 | Nitrogen, Total | 64 | LBS/DAY
1999-11-30 | Phosphorus, Total (as P) | 4 | LBS/DAY
1999-11-30 | Phosphorus, Total (as P) | 0.07 | MG/L
1999-11-30 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-11-30 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 1 | #/100ML
1999-11-30 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 2 | #/100ML
1999-11-30 | Oxygen, Dissolved (DO) | 5.9 | MG/L
1999-11-30 | Oxygen, Dissolved (DO) | 5.9 | MG/L
1999-11-30 | Chlorine, Total Residual | 0.6 | MG/L
1999-11-30 | Chlorine, Total Residual | 3.5 | MG/L
1999-11-30 | Solids, Total Suspended | 1.5 | MG/L
1999-11-30 | Chlorine, Total Residual | 1.5 | MG/L
1999-11-30 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-08-31 | Flow, Wwtp, Monthly Average | 12.65 | MGD
1999-08-31 | Flow, Wwtp, Monthly Average | 8.75 | MGD
1999-08-31 | BOD, Carbonaceous 5 day, 20C | 117 | MG/L
1999-08-31 | BOD, Carbonaceous 5 day, 20C | 418 | MG/L
1999-08-31 | Solids, Total Suspended | 945 | MG/L
1999-08-31 | Solids, Total Suspended | 163 | MG/L
1999-08-31 | BOD, Carbonaceous 5 day, 20C | 6 | MG/L
1999-08-31 | BOD, Carbonaceous 5 day, 20C | 2.1 | MG/L
1999-08-31 | BOD, Carbonaceous 5 day, 20C | 2.1 | MG/L
1999-08-31 | Solids, Total Suspended | 17.6 | MG/L
1999-08-31 | Solids, Total Suspended | 5.8 | MG/L
1999-08-31 | Solids, Total Suspended | 7 | MG/L
1999-08-31 | pH | 7.3 | SU
1999-08-31 | pH | 6.5 | SU
1999-08-31 | Nitrogen, Total | 1.66 | MG/L
1999-08-31 | Nitrogen, Total | 106 | LBS/DAY
1999-08-31 | Phosphorus, Total (as P) | 0.07 | MG/L
1999-08-31 | Phosphorus, Total (as P) | 4 | LBS/DAY
1999-08-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-08-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-08-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 2 | #/100ML
1999-08-31 | Oxygen, Dissolved (DO) | 5 | MG/L
1999-08-31 | Oxygen, Dissolved (DO) | 5 | MG/L
1999-08-31 | Chlorine, Total Residual | 0.6 | MG/L
1999-08-31 | Chlorine, Total Residual | <0.01 | MG/L
1999-08-31 | Solids, Total Suspended | 2.8 | MG/L
1999-08-31 | Chlorine, Total Residual | 1.5 | MG/L
1999-08-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-05-31 | Flow, Wwtp, Monthly Average | 5.64 | MGD
1999-05-31 | Flow, Wwtp, Monthly Average | 6.38 | MGD
1999-05-31 | BOD, Carbonaceous 5 day, 20C | 181 | MG/L
1999-05-31 | BOD, Carbonaceous 5 day, 20C | 248 | MG/L
1999-05-31 | Solids, Total Suspended | 285 | MG/L
1999-05-31 | Solids, Total Suspended | 198 | MG/L
1999-05-31 | BOD, Carbonaceous 5 day, 20C | 1.9 | MG/L
1999-05-31 | BOD, Carbonaceous 5 day, 20C | 2.5 | MG/L
1999-05-31 | BOD, Carbonaceous 5 day, 20C | 2.2 | MG/L
1999-05-31 | Solids, Total Suspended | 6.8 | MG/L
1999-05-31 | Solids, Total Suspended | 4.5 | MG/L
1999-05-31 | Solids, Total Suspended | 6.4 | MG/L
1999-05-31 | pH | 6 | SU
1999-05-31 | pH | 7.4 | SU
1999-05-31 | Solids, Total Suspended | 1.8 | MG/L
1999-05-31 | Chlorine, Total Residual | 1.5 | MG/L
1999-05-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-03-31 | Flow, Wwtp, Monthly Average | 5.75 | MGD
1999-03-31 | Flow, Wwtp, Monthly Average | 6.24 | MGD
1999-03-31 | BOD, Carbonaceous 5 day, 20C | 186 | MG/L
1999-03-31 | BOD, Carbonaceous 5 day, 20C | 349 | MG/L
1999-03-31 | Solids, Total Suspended | 199 | MG/L
1999-03-31 | Solids, Total Suspended | 421 | MG/L
1999-03-31 | BOD, Carbonaceous 5 day, 20C | 7 | MG/L
1999-03-31 | BOD, Carbonaceous 5 day, 20C | 2.3 | MG/L
1999-03-31 | BOD, Carbonaceous 5 day, 20C | 3.4 | MG/L
1999-03-31 | Solids, Total Suspended | 9.8 | MG/L
1999-03-31 | Solids, Total Suspended | 28 | MG/L
1999-03-31 | Solids, Total Suspended | 6.9 | MG/L
1999-03-31 | pH | 6.1 | SU
1999-03-31 | pH | 7.3 | SU
1999-03-31 | Nitrogen, Total | 2.88 | MG/L
1999-03-31 | Nitrogen, Total | 121 | LBS/DAY
1999-03-31 | Phosphorus, Total (as P) | 0.13 | MG/L
1999-03-31 | Phosphorus, Total (as P) | 5 | LBS/DAY
1999-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.1 | #/100ML
1999-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | 2 | #/100ML
1999-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <2.0 | #/100ML
1999-03-31 | Oxygen, Dissolved (DO) | 6.1 | MG/L
1999-03-31 | Oxygen, Dissolved (DO) | 6.1 | MG/L
1999-03-31 | Chlorine, Total Residual | 1.4 | MG/L
1999-03-31 | Chlorine, Total Residual | <0.001 | MG/L
1999-03-31 | Solids, Total Suspended | 1.8 | MG/L
1999-03-31 | Chlorine, Total Residual | 1.5 | MG/L
1999-03-31 | Coliform, Fecal Mf, M-Fc Broth,44 5c | <1.0 | #/100ML
1999-03-31 | Water Level Relative to NGVD | anc | FEET
1999-03-31 | Nitrogen, Nitrate, Total (as N) | <.01 | MG/L
1999-03-31 | Solids, Total Dissolved (TDS) | 374 | MG/L
1999-03-31 | Chloride (as Cl) | 65 | MG/L
1999-03-31 | Coliform, Fecal | <2 | #/100ML
1999-03-31 | pH | anc | SU
1999-03-31 | Sulfate, Total | 10 | MG/L
1999-03-31 | Specific Conductance | mnr | UMHO/CM
1999-03-31 | Sodium, Total Recoverable | mnr | MG/L
1999-03-31 | Trihalomethane, Total by summation | mnr | MG/L
1999-03-31 | Water Level Relative to NGVD | anc | FEET
1999-03-31 | Nitrogen, Nitrate, Total (as N) | <.01 | MG/L
1999-03-31 | Solids, Total Dissolved (TDS) | 428 | MG/L
1999-03-31 | Chloride (as Cl) | 19 | MG/L
1999-03-31 | Coliform, Fecal | <2 | #/100ML
1999-03-31 | pH | anc | SU
1999-03-31 | Sulfate, Total | 13 | MG/L
1999-03-31 | Specific Conductance | mnr | UMHO/CM
1999-03-31 | Sodium, Total Recoverable | mnr | MG/L
1999-03-31 | Trihalomethane, Total by summation | mnr | MG/L
1999-03-31 | Water Level Relative to NGVD | anc | FEET
1999-03-31 | Nitrogen, Nitrate, Total (as N) | <.01 | MG/L
1999-03-31 | Solids, Total Dissolved (TDS) | 474 | MG/L
1999-03-31 | Chloride (as Cl) | 38.5 | MG/L
1999-03-31 | Coliform, Fecal | <2 | #/100ML
1999-03-31 | pH | anc | SU
1999-03-31 | Sulfate, Total | 58 | MG/L
1999-03-31 | Specific Conductance | mnr | UMHO/CM
1999-03-31 | Sodium, Total Recoverable | mnr | MG/L
1999-03-31 | Trihalomethane, Total by summation | mnr | MG/L