## MOST RECENT_10-29-2014
Summary of Options
Facility | Area (Acres) | FDOT to provide Design, Const. and Maintenance | Phosphorous Removal (kg/yr) | Phosphorous Removal (MT/yr) | Sub-basin | Attenuation Factor | TP Reduction w/Attenuation (kg/yr) |  | TP Reduction w/Attenuation (MT/yr)
Regional Pond Opt A | 26 | Yes | 496 | 0.496 | Taylor Creek - S131 | 0.158 | 417.632 |  | 0.41763
Regional Pond Opt B | 26 | Yes/No | 168-788 | .168-.788 | Taylor Creek - S131 | 0.158 | 141.456 | 663.496 | 0.14146 | 0.6635
STA – Option 1 | 60 | No | Up to 727 | Up to .727 | Taylor Creek - S131 | 0.158 | 612.134 |  | 0.61213
Biosorption - Option 2 | 0* | No | Up to 176 | Up to .176 | Taylor Creek - S131 | 0.158 | 148.192 |  | 0.14819
Rehydration – Option 3 | 162.5 | No | Up to 144 | Up to .144 | Taylor Creek - S131 | 0.158 | 121.248 |  | 0.12125
*May be located in existing SFWMD Easement
[7 empty] | 121.248-663.496 |  | 0.121-0.663 |  | Range

## 2014 TC_STA_Rpt
Parameter | WY2009 | WY2011 | WY2012 | WY2013 | Total | Area | 118 | AC
Period of operation, days | 244 | 235 | 366 | 276
Total inflow, ac-ft | 9218 | 6988 | 13188 | 5810
Hydraulic loading rate, cm/d | 9.7585 | 7.6811 | 9.3076 | 5.4376
Inflow TP, ug/L | 408 | 167 | 341 | 368
Total Load In, MT | 4.6391 | 1.4395 | 5.5471 | 2.6373 | 14.2629
TP mass load rate, g/m2/d | 0.039815 | 0.012827 | 0.031739 | 0.02001
Total outflow, ac-ft | 8767 | 6257 | 12208 | 5762
Outflow/Inflow, % | 95.11% | 89.54% | 92.57% | 99.17%
Outflow TP, ug/L | 295 | 68 | 292 | 289
Total Load Out, MT | 3.1901 | 0.52482 | 4.397 | 2.054 | 10.166
HRT, d | 6.34 | 7.75 | 6.52 | 9.72
TP mass removed, MT | 1.4489 | 0.91465 | 1.1501 | 0.58327 | 4.0969
TP Conc reduction | 27.7% | 59.28% | 14.37% | 21.47%
TP Load Reduction | 31.23% | 63.54% | 20.73% | 22.12% | 28.72%

## Calcs
Parameter | Scen 1 | Scen 2 | Scen 3 | Scen 4
STA acreage | 100 | 100 | 100 | 100
Period of operation, days | 365 | 365 | 365 | 365
Total inflow, ac-ft | 7184.952 | 9579.936 | 11974.92 | 14369.904
Hydraulic loading rate, cm/d | 6 | 8 | 10 | 12 |  |  | Hydraulic loading rate, cm/d
Inflow TP, ug/L | 439 | 439 | 439 | 439 |  | 38% | 6 | 8 | 10 | 12
Total Load In, MT | 3.8906 | 5.1875 | 6.4844 | 7.7813 | TP removed, MT | 439 | 1.4784 | 1.9713 | 2.4641 | 2.9569
TP mass load rate, g/m2/d | 0.02634 | 0.03512 | 0.0439 | 0.05268
Total outflow, ac-ft | 6825.7044 | 9100.9392 | 11376.174 | 13651.4088
Outflow/Inflow, % | 95% | 95% | 95% | 95%
Assumed % TP load reduction | 38% | 38% | 38% | 38%
Total Load Out, MT | 2.4122 | 3.2163 | 4.0203 | 4.8244
TP mass removed, MT | 1.4784 | 1.9713 | 2.4641 | 2.9569
Assumed % TP load reduction | 20% | 20% | 20% | 20%
Total Load Out, MT | 3.1125 | 4.15 | 5.1875 | 6.225
TP mass removed, MT | 0.77813 | 1.0375 | 1.2969 | 1.5563
Assumed % TP load reduction | 28.7% | 28.7% | 28.7% | 28.7%
Total Load Out, MT | 2.774 | 3.6987 | 4.6234 | 5.5481
TP mass removed, MT | 1.1166 | 1.4888 | 1.861 | 2.2332
TP is annual geometric mean at Taylor Cr at Cemetary Rd, 2008, 2009, 2010, 2011

## Calcs (2)
Parameter | Scen 1 | Scen 2 | Scen 3 | Scen 4
STA acreage | 100 | 100 | 100 | 100
Period of operation, days | 365 | 365 | 365 | 365
Total inflow, ac-ft | 7184.952 | 9579.936 | 11974.92 | 14369.904
Hydraulic loading rate, cm/d | 6 | 8 | 10 | 12
Inflow TP, ug/L | 343 | 343 | 343 | 343
Total Load In, MT | 3.0398 | 4.0531 | 5.0664 | 6.0797
TP mass load rate, g/m2/d | 0.02058 | 0.02744 | 0.0343 | 0.04116
Total outflow, ac-ft | 6825.7044 | 9100.9392 | 11376.174 | 13651.4088
Outflow/Inflow, % | 95% | 95% | 95% | 95%
Assumed % TP load reduction | 38% | 38% | 38% | 38%
Total Load Out, MT | 1.8847 | 2.5129 | 3.1412 | 3.7694
TP mass removed, MT | 1.1551 | 1.5402 | 1.9252 | 2.3103
Assumed % TP load reduction | 20% | 20% | 20% | 20%
Total Load Out, MT | 2.4319 | 3.2425 | 4.0531 | 4.8637
TP mass removed, MT | 0.60797 | 0.81062 | 1.0133 | 1.2159
Assumed % TP load reduction | 28.7% | 28.7% | 28.7% | 28.7%
Total Load Out, MT | 2.1674 | 2.8899 | 3.6123 | 4.3348
TP mass removed, MT | 0.87243 | 1.1632 | 1.4541 | 1.7449

## Calcs (3)
Parameter | Scen 1 | Scen 2 | Scen 3 | Scen 4
STA acreage | 100 | 100 | 100 | 100
Period of operation, days | 365 | 365 | 365 | 365
Total inflow, ac-ft | 7184.952 | 9579.936 | 11974.92 | 14369.904
Hydraulic loading rate, cm/d | 6 | 8 | 10 | 12
Inflow TP, ug/L | 334 | 334 | 334 | 334
Total Load In, MT | 2.9601 | 3.9468 | 4.9335 | 5.9202
TP mass load rate, g/m2/d | 0.02004 | 0.02672 | 0.0334 | 0.04008
Total outflow, ac-ft | 6825.7044 | 9100.9392 | 11376.174 | 13651.4088
Outflow/Inflow, % | 95% | 95% | 95% | 95%
Assumed % TP load reduction | 38% | 38% | 38% | 38%
Total Load Out, MT | 1.8352 | 2.447 | 3.0587 | 3.6705
TP mass removed, MT | 1.1248 | 1.4998 | 1.8747 | 2.2497
Assumed % TP load reduction | 20% | 20% | 20% | 20%
Total Load Out, MT | 2.3681 | 3.1574 | 3.9468 | 4.7361
TP mass removed, MT | 0.59202 | 0.78935 | 0.98669 | 1.184
Assumed % TP load reduction | 28.7% | 28.7% | 28.7% | 28.7%
Total Load Out, MT | 2.1105 | 2.814 | 3.5176 | 4.2211
TP mass removed, MT | 0.84954 | 1.1327 | 1.4159 | 1.6991

## Calcs (4)
Parameter | Scen 1 | Scen 2 | Scen 3 | Scen 4
STA acreage | 100 | 100 | 100 | 100
Period of operation, days | 365 | 365 | 365 | 365
Total inflow, ac-ft | 7184.952 | 9579.936 | 11974.92 | 14369.904
Hydraulic loading rate, cm/d | 6 | 8 | 10 | 12
Inflow TP, ug/L | 298 | 298 | 298 | 298
Total Load In, MT | 2.641 | 3.5214 | 4.4017 | 5.2821
TP mass load rate, g/m2/d | 0.01788 | 0.02384 | 0.0298 | 0.03576
Total outflow, ac-ft | 6825.7044 | 9100.9392 | 11376.174 | 13651.4088
Outflow/Inflow, % | 95% | 95% | 95% | 95%
Assumed % TP load reduction | 38% | 38% | 38% | 38%
Total Load Out, MT | 1.6374 | 2.1832 | 2.7291 | 3.2749
TP mass removed, MT | 1.0036 | 1.3381 | 1.6727 | 2.0072
Assumed % TP load reduction | 20% | 20% | 20% | 20%
Total Load Out, MT | 2.1128 | 2.8171 | 3.5214 | 4.2256
TP mass removed, MT | 0.52821 | 0.70427 | 0.88034 | 1.0564
Assumed % TP load reduction | 28.7% | 28.7% | 28.7% | 28.7%
Total Load Out, MT | 1.8831 | 2.5107 | 3.1384 | 3.7661
TP mass removed, MT | 0.75797 | 1.0106 | 1.2633 | 1.5159

## Summary
38% mass removal |  | Hydraulic loading rate, cm/d |  |  |  | 28.7% mass removal |  | Hydraulic loading rate, cm/d |  |  |  | 20% mass removal |  | Hydraulic loading rate, cm/d
|  | 6 | 8 | 10 | 12 |  |  | 6 | 8 | 10 | 12 |  |  | 6 | 8 | 10 | 12
Annual TP Geomean, µg/L | 439 | 1.4784 | 1.9713 | 2.4641 | 2.9569 | Annual TP Geomean, µg/L | 439 | 1.1166 | 1.4888 | 1.861 | 2.2332 | Annual TP Geomean, µg/L | 439 | 0.77813 | 1.0375 | 1.2969 | 1.5563
| 343 | 1.1551 | 1.5402 | 1.9252 | 2.3103 |  | 343 | 0.87243 | 1.1632 | 1.4541 | 1.7449 |  | 343 | 0.60797 | 0.81062 | 1.0133 | 1.2159
| 334 | 1.1248 | 1.4998 | 1.8747 | 2.2497 |  | 334 | 0.84954 | 1.1327 | 1.4159 | 1.6991 |  | 334 | 0.59202 | 0.78935 | 0.98669 | 1.184
| 298 | 1.0036 | 1.3381 | 1.6727 | 2.0072 |  | 298 | 0.75797 | 1.0106 | 1.2633 | 1.5159 |  | 298 | 0.52821 | 0.70427 | 0.88034 | 1.0564
Design efficiency | [5 empty] | Measured efficiency | [5 empty] | Minimum efficiency
1. Input TP concentrations are annual geometeric means for 2011, 2010, 2009, 2008 at station Taylor Creek at Cemetary Rd
2. Assumes annual period of operation is 365 days
3. Assumes treatment area of 100 acres