## Background (Parts 1 & 2)
Municipality | City of Eustis
Facility Name | Bates Ave WWTF
Permitted Capacity in Avg Annual Gallons Per Day |  | 2.4 | MGD
WWTF Upgrade is currently under construction. Upon completion of the upgrade, Permitted Capacity will be 2.99 MGD.
Permitted TN Effluent Limits |  | Nitrogen, Nitrate, Total (as N) mg/L Max 10.0 Single Sample
Permitted TP Effluent Limits |  | Phosphorus, Total (as P) mg/L. Max (Report) Annual Average = 4.3

## Annual TN & TP Loads (Part 3)
BATES WWTF
(FLOWxCONCENTRATION)x8.34
ANNUAL LOADS
DATE | FLOW (MG) | TN (mg/L) | TP (mg/L) | TN (lbs) | TP (lbs) | Year | TN (lbs) | TP (lbs)
2018-11-01 | 1.3281 | 5.1 | 2 | 56.488 | 22.1522 | 2019 | 75.1939 | 51.6745
2018-12-01 | 1.3773 | 5.1 | 4.3 | 58.583 | 49.3935 | 2020 | 48.1789 | 44.3972
2019-01-01 | 1.4684 | 6.9 | 3.6 | 84.4998 | 44.0869 | 2021 | 66.1534 | 40.952
2019-02-01 | 1.4596 | 5.2 | 8.4 | 63.3018 | 102.2567 | 2022 | 82.5858 | 65.2801
2019-03-01 | 1.3113 | 5.9 | 3.2 | 64.5234 | 34.9957 | 2023 | 83.1753 | 53.1124
2019-04-01 | 1.2879 | 8.2 | 5.8 | 88.0792 | 62.2999
2019-05-01 | 0.82735 | 6.62 | 3.9 | 45.6789 | 26.9105
2019-06-01 | 1.3781 | 7.5 | 4.2 | 86.1981 | 48.2709 | ANNUAL LOADS
2019-07-01 | 1.4824 | 4.85 | 4.35 | 59.9624 | 53.7807 | Year | TN (mg/L) | TP (mg/L)
2019-08-01 | 1.6787 | 6.2 | 3.6 | 86.8044 | 50.4025 | 2019 | 6.4058 | 4.3567
2019-09-01 | 1.7194 | 7.6 | 5.4 | 108.9803 | 77.4334 | 2020 | 4.0133 | 3.7167
2019-10-01 | 1.5108 | 7.3 | 6 | 91.979 | 75.5991 | 2021 | 6.3483 | 3.8492
2019-11-01 | 1.3743 | 6.8 | 3.1 | 77.9412 | 35.532 | 2022 | 6.7417 | 5.3417
2019-12-01 | 1.4003 | 3.8 | 0.73 | 44.379 | 8.5254 | 2023 | 6.4833 | 4.1917
2020-01-01 | 1.451 | 5 | 1.4 | 60.5054 | 16.9415
2020-02-01 | 1.3941 | 4.3 | 2.6 | 49.9966 | 30.2305
2020-03-01 | 1.389 | 4 | 2.8 | 46.3381 | 32.4367
2020-04-01 | 1.2883 | 3.16 | 3.5 | 33.9533 | 37.6064
2020-05-01 | 1.2374 | 3.2 | 5.7 | 33.0234 | 58.8229
2020-06-01 | 1.5277 | 2.6 | 4 | 33.1259 | 50.963
2020-07-01 | 1.4132 | 4 | 5.3 | 47.1452 | 62.4674
2020-08-01 | 1.5067 | 3.6 | 6.5 | 45.2384 | 81.6805
2020-09-01 | 1.7283 | 5.1 | 3.7 | 73.5129 | 53.3329
2020-10-01 | 1.5055 | 4.6 | 3.1 | 57.7564 | 38.9228
2020-11-01 | 1.4077 | 4.8 | 4.8 | 56.3517 | 56.3517
2020-12-01 | 1.3 | 3.8 | 1.2 | 41.1996 | 13.0104
2021-01-01 | 1.1632 | 7.2 | 4.2 | 69.8494 | 40.7455
2021-02-01 | 1.3271 | 9.78 | 4.79 | 108.2487 | 53.0175
2021-03-01 | 1.2542 | 5.8 | 2.8 | 60.6679 | 29.2879
2021-04-01 | 1.3567 | 4.6 | 3.2 | 52.0472 | 36.2067
2021-05-01 | 1.2332 | 7 | 7 | 71.9957 | 71.9957
2021-06-01 | 1.3173 | 3.7 | 3.1 | 40.6503 | 34.0583
2021-07-01 | 1.4077 | 5.3 | 3.1 | 62.225 | 36.3958
2021-08-01 | 1.3077 | 4.9 | 4 | 53.4395 | 43.6241
2021-09-01 | 1.0755 | 16 | 4 | 143.5192 | 35.8798
2021-10-01 | 1.2977 | 4.4 | 3.2 | 47.6219 | 34.6341
2021-11-01 | 1.3817 | 3.4 | 2.8 | 39.1785 | 32.2647
2021-12-01 | 1.2984 | 4.1 | 4 | 44.397 | 43.3142
2022-01-01 | 1.3826 | 6.6 | 7.4 | 76.1028 | 85.3273
2022-02-01 | 1.5664 | 5.3 | 8.5 | 69.2393 | 111.0441
2022-03-01 | 1.4477 | 7.2 | 8.1 | 86.934 | 97.8008
2022-04-01 | 1.3852 | 7.2 | 5 | 83.1805 | 57.7642
2022-05-01 | 1.3677 | 6.1 | 4.4 | 69.5825 | 50.1907
2022-06-01 | 1.2997 | 6.2 | 6 | 67.2032 | 65.0353
2022-07-01 | 1.4171 | 7.4 | 5.1 | 87.4575 | 60.2748
2022-08-01 | 1.4084 | 7.7 | 3.9 | 90.4438 | 45.8092
2022-09-01 | 1.58 | 8.7 | 4.9 | 114.6416 | 64.5683
2022-10-01 | 1.6532 | 5.3 | 3.2 | 73.0759 | 44.1213
2022-11-01 | 1.6637 | 7 | 5.1 | 97.1249 | 70.7624
2022-12-01 | 1.4706 | 6.2 | 2.5 | 76.0441 | 30.663
2023-01-01 | 1.4658 | 7.6 | 4.3 | 92.9087 | 52.5668
2023-02-01 | 1.3571 | 7.7 | 6.4 | 87.153 | 72.4389
2023-03-01 | 1.4355 | 6 | 3.4 | 71.8316 | 40.7046
2023-04-01 | 1.4729 | 4.6 | 4.9 | 56.5063 | 60.1915
2023-05-01 | 1.4484 | 6 | 5.2 | 72.4773 | 62.8137
2023-06-01 | 1.4943 | 6.3 | 4.6 | 78.5153 | 57.3286
2023-07-01 | 1.6571 | 8.7 | 4 | 120.2356 | 55.2807
2023-08-01 | 1.509 | 6.3 | 3.8 | 79.2876 | 47.8243
2023-09-01 | 1.6289 | 5 | 4.2 | 67.9237 | 57.0559
2023-10-01 | 1.6216 | 7.8 | 4.2 | 105.4892 | 56.8019
2023-11-01 | 1.669 | 5.9 | 3.1 | 82.1248 | 43.1503
2023-12-01 | 1.7 | 5.9 | 2.2 | 83.6502 | 31.1916

## Capacity Analysis (Part 4)
See Bates WWTF Capacity Analysis PDF attachment

## Projects (Parts 5 & 6)
Estimated Expenditures (in thousands $)
Project Name | Project Ranking | Planned Years | FY 2023-24 to 2027-28 | FY 2028-29 to 2032-33 | FY 2033-34 to 2037-38 | FY 2038-39 to 2042-43 | Projected Begin Year | Projected Completion Year | Projected Operations Begin Year
Bates WWTP Expansion (BMAP OKLA, Project IDs 5379, 6643, and 7033) | 1 | Currently Under Construction | 10800 |  |  |  | 2023 | 2024 | 2024
Lift Station 9 (BMAP OKLA, Project ID 6393) | 2 | Currently Under Construction | 540 |  |  |  | 2023 | 2024 | 2024
Lift Station 3 Generator | 3 | Currently Under Construction | 93 |  |  |  | 2023 | 2025 | 2025
Coolidge Sewer Main Expansion (BMAP OKLA, Project ID 7034) | 4 | 23-24(Const) | 1800 |  |  |  | 2023 | 2025 | 2025
Sewer Mains: Inspection/Rehab/Sliplining/Inflow & Infiltration (BMAP OKLA, Current Project ID 7041) | 5 | Ongoing | 760 | 1100 | 1400 | 1500 | Ongoing | Ongoing | Ongoing
CR44 Force Main Upsize & Replace | 6 | 23-24(Design) & 25-26(Const) | 430 |  |  |  | 2024 | 2026 | 2026
Bates Ave Plant Sewer Upgrade | 7 | 24-25(Design) & 26-27(Const) | 120 |  |  |  | 2024 | 2028 | 2028
Master Liftstation Motor Control Upgrade | 8 | 24-25(Engineer) & 26-27(Const) | 360 |  |  |  | 2024 | 2028 | 2028
Process & Clarification Tank Rehabilitation | 9 | 26-27(Engineer) & 28-29(Const) | 120 | 1400 |  |  | 2026 | 2030 | 2030
Bates WWTP Improvements for Capacity Expansion | 10 | 29-30(Start) |  | 12500 | 7000 |  | 2029 | 2039 | 2039
Wastewater Masterplan Projects - Liftstations | 11 | 27-28(Start) | $100 (Engineer) | 3040 |  |  | 2027 | 2033 | 2033
Wastewater Masterplan Projects - Force Mains | 11 | 27-28(Start) | $100 (Engineer) | 1883 | 2822 | 4281 | 2027 | 2043 | 2043
Wastewater Masterplan Projects - Gravity Mains | 11 | 27-28(Start) | $50 (Engineer) | 7641 |  | 1539 | 2027 | 2043 | 2043