## Background (Parts 1 & 2)
Municipality | City of Eustis
Facility Name | Eastern WWTF
Permitted Capacity in Avg Annual Gallons Per Day |  | 1.3 | MGD
Permitted TN Effluent Limits |  | Nitrogen, Nitrate, Total (as N) mg/L Max 10.0 Single Sample
Permitted TP Effluent Limits |  | Phosphorus, Total (as P) mg/L. Max (Report) Annual Average = 4.4

## Annual TN & TP Loads (Part 3)
Eastern WWTF
(FLOWxCONCENTRATION)x8.34
DATE | FLOW (MG) | TN (mg/L) | TP (mg/L) | TN (lbs) | TP (lbs) | ANNUAL LOADS
2018-11-01 | 2.578 | 7 | 5.8 | 150.5036 | 124.703 | Year | TN (lbs) | TP (lbs)
2018-12-01 | 0 | 0 | 0 | 0 | 0 | 2019 | 312.994 | 141.5277
2019-01-01 | 0.704 | 1.4 | 1.7 | 8.2199 | 9.9813 | 2020 | 98.3434 | 127.3205
2019-02-01 | 1.91 | 2 | 0.8 | 31.8588 | 12.7435 | 2021 | 66.7351 | 138.6795
2019-03-01 | 4.499 | 9.5 | 1.5 | 356.4558 | 56.2825 | 2022 | 156.0961 | 197.1921
2019-04-01 | 5.438 | 17.9 | 4.7 | 811.8173 | 213.1587 | 2023 | 70.3505 | 231.6835
2019-05-01 | 5.326 | 4.6 | 6.1 | 204.3267 | 270.9549
2019-06-01 | 5.027 | 0.8 | 3.7 | 33.5401 | 155.1232
2019-07-01 | 3.199 | 3.9 | 3.2 | 104.0507 | 85.3749 | ANNUAL LOADS
2019-08-01 | 4.729 | 15.7 | 4.6 | 619.2058 | 181.4234 | Year | TN (mg/L) | TP (mg/L)
2019-09-01 | 4.77 | 13 | 6.6 | 517.1634 | 262.5599 | 2019 | 7.6608 | 3.5392
2019-10-01 | 5.486 | 9.3 | 3.8 | 425.5051 | 173.8623 | 2020 | 2.4333 | 3.1583
2019-11-01 | 6.14 | 7.7 | 4 | 394.2985 | 204.8304 | 2021 | 1.5479 | 3.275
2019-12-01 | 4.88 | 6.13 | 1.77 | 249.4861 | 72.0376 | 2022 | 3.1167 | 3.9
2020-01-01 | 4.88 | 14.8 | 5.6 | 602.3482 | 227.9155 | 2023 | 1.3583 | 4.5167
2020-02-01 | 4.79 | 9.5 | 4.7 | 379.5117 | 187.7584
2020-03-01 | 4.917 | 0.6 | 1.2 | 24.6047 | 49.2093
2020-04-01 | 4.671 | 0.3 | 1 | 11.6868 | 38.9561
2020-05-01 | 4.751 | 0.3 | 3.9 | 11.887 | 154.531
2020-06-01 | 4.608 | 0.3 | 3.3 | 11.5292 | 126.8214
2020-07-01 | 4.769 | 0.3 | 3.5 | 11.932 | 139.2071
2020-08-01 | 4.846 | 0.3 | 3.5 | 12.1247 | 141.4547
2020-09-01 | 5.034 | 0.7 | 5.5 | 29.3885 | 230.9096
2020-10-01 | 4.967 | 0.4 | 2.7 | 16.5699 | 111.8469
2020-11-01 | 4.676 | 0.9 | 2.2 | 35.0981 | 85.7952
2020-12-01 | 5.012 | 0.8 | 0.8 | 33.4401 | 33.4401
2021-01-01 | 4.7 | 0.6 | 1 | 23.5188 | 39.198
2021-02-01 | 4.493 | 0.775 | 4.5 | 29.0405 | 168.6223
2021-03-01 | 4.936 | 1.2 | 3.4 | 49.3995 | 139.9652
2021-04-01 | 4.761 | 0.7 | 3 | 27.7947 | 119.1202
2021-05-01 | 4.952 | 1.1 | 2.8 | 45.4296 | 115.6391
2021-06-01 | 5.055 | 1 | 4 | 42.1587 | 168.6348
2021-07-01 | 4.842 | 1.1 | 2.4 | 44.4205 | 96.9175
2021-08-01 | 5.09 | 4.5 | 4 | 191.0277 | 169.8024
2021-09-01 | 5.52 | 2.2 | 3.6 | 101.281 | 165.7325
2021-10-01 | 5.615 | 3.2 | 4.6 | 149.8531 | 215.4139
2021-11-01 | 4.848 | 1 | 2.6 | 40.4323 | 105.124
2021-12-01 | 5.642 | 1.2 | 3.4 | 56.4651 | 159.9846
2022-01-01 | 5.866 | 8.4 | 7.8 | 410.9485 | 381.595
2022-02-01 | 5.339 | 2.4 | 4.2 | 106.8654 | 187.0145
2022-03-01 | 6.986 | 1.7 | 5.4 | 99.0475 | 314.6215
2022-04-01 | 6.081 | 1.5 | 2 | 76.0733 | 101.4311
2022-05-01 | 6.174 | 1.3 | 2.2 | 66.9385 | 113.2806
2022-06-01 | 5.838 | 2.5 | 4.7 | 121.7223 | 228.8379
2022-07-01 | 5.978 | 2 | 4.3 | 99.713 | 214.383
2022-08-01 | 6.377 | 1.7 | 4.1 | 90.4131 | 218.0551
2022-09-01 | 6.439 | 6.5 | 4.2 | 349.0582 | 225.5453
2022-10-01 | 5.962 | 2.3 | 3.5 | 114.3631 | 174.0308
2022-11-01 | 6.282 | 4 | 2.3 | 209.5675 | 120.5013
2022-12-01 | 4.968 | 3.1 | 2.1 | 128.4427 | 87.0096
2023-01-01 | 7.367 | 1.3 | 2.7 | 79.873 | 165.8901
2023-02-01 | 6.509 | 2.9 | 4.2 | 157.4267 | 227.9973
2023-03-01 | 4.946 | 2.3 | 6.5 | 94.8742 | 268.1227
2023-04-01 | 6.071 | 1.1 | 8.4 | 55.6954 | 425.31
2023-05-01 | 6.721 | 1 | 4.2 | 56.0531 | 235.4232
2023-06-01 | 6.196 | 1 | 3.1 | 51.6746 | 160.1914
2023-07-01 | 6.463 | 2 | 5.9 | 107.8028 | 318.0184
2023-08-01 | 6.204 | 1.2 | 4.3 | 62.0896 | 222.4878
2023-09-01 | 6.095 | 0.6 | 3.2 | 30.4994 | 162.6634
2023-10-01 | 6.121 | 0.7 | 4.4 | 35.7344 | 224.6162
2023-11-01 | 5.77 | 1 | 4 | 48.1218 | 192.4872
2023-12-01 | 6.431 | 1.2 | 3.3 | 64.3614 | 176.994

## Capacity Analysis (Part 4)
See Eastern WWTF Capacity Analysis PDF attachment

## Projects (Parts 5 & 6)
Estimated Expenditures (in thousands $)
Project Name | Project Ranking | Planned Years | FY 2023-24 to 2027-28 | FY 2028-29 to 2032-33 | FY 2033-34 to 2037-38 | FY 2038-39 to 2042-43 | Projected Begin Year | Projected Completion Year | Projected Operations Begin Year
Eastern Force Main Extension & Upsizing | 1 | 23-24(Const) | 400 |  |  |  | 2024 | 2025 | 2025
Influent Pump - Eastern WWTF Capacity | 2 | 26-27(Engineer) & 28-29(Const) | 40 | 200 |  |  | 2026 | 2030 | 2030