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	July 6, 2007

	
	EXPIRATION DATE:
	July 5, 2012

	RESPONSIBLE AUTHORITY:
	
	

	
	
	

	Mr. John A. Peters, III, P.E.

	City Engineer

	225 Newburyport Avenue

	Altamonte Springs, FL 32701


(407) 571-8338
FACILITY:

	Altamonte Springs Regional WRF

	950 Keller Road

	Altamonte Springs, FL  32701

	Seminole County


Latitude: 28° 38’ 32” N      Longitude: 81° 23’ 56” W
This permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and applicable rules of the Florida Administrative Code (F.A.C.) and constitutes authorization to discharge to waters of the state under the National Pollutant Discharge Elimination System. This permit is accompanied by an Administrative Order, pursuant to paragraphs 403.088(2)(e) and (f), Florida Statutes. Compliance with Administrative Order, 06-2162 is a specific requirement of this permit.   The above named permittee is hereby authorized to operate the facilities shown on the application and other documents attached hereto or on file with the Department and made a part hereof and specifically described as follows:

TREATMENT FACILITIES:

An existing 12.5 MGD annual average daily flow (AADF) permitted capacity activated sludge advanced domestic wastewater treatment plant consisting of influent screening, grit removal, primary sedimentation, anoxic/aerobic nitrification, secondary clarification, flocculation, denitrification, filtration, a chemical feed system, post aeration, chlorination, dechlorination/neutralization, and one (1) 0.25 million gallon (MG) effluent holding tank, with aerobic digestion of residuals followed by gravity thickening and belt filter press dewatering.  

DISPOSAL:

Surface Water Discharge An existing 12.5 mgd AADF permitted discharge to Little Wekiva River (Class III freshwater that has been designated as an Outstanding Florida Water) at the outfall, Discharge Location (D-001), which is approximately 15,840 feet in length from the plant (zero distance from the shoreline) and discharges at a depth of approximately 2 feet.  The point of discharge is located approximately at latitude 28SYMBOL 176 \f "Symbol" 39' 15" N, longitude 81SYMBOL 176 \f "Symbol" 24' 26" W.

REUSE:

Land Application:  An existing 12.5 mgd AADF permitted capacity slow-rate public access system (R-001) consisting of a reclaimed water transmission and distribution system to provide reclaimed water throughout the City of Altamonte Springs for irrigation, within the 5,900 acre Reuse Service Area, of city parks, street and highway medians, city owned nurseries, residential and commercial lawns, as shown in the attached Reuse System Map. Reclaimed water is also used for street cleaning, dust control, fire protection, water-to-air heat pumps, chillers (cooling water towers) and at automatic car washers. The public access reuse system includes two (2) existing 3 MG reclaimed water storage tanks, and one (1) publicly owned storage pond known as Cranes Roost.  The city may direct wet weather flows to discharge location D001.

The following surface water sources may be introduced into the sanitary sewer system to augment the supply of reclaimed water:  Lake Orienta, Lake Maltbie, and Cranes Roost. 

The following ground water sources may be used to augment the supply of reclaimed water:  The former water supply wells at Water Treatment Plant #3, no longer used as a potable source. 

Stormwater from the following sources may be introduced into the sanitary sewerage system to augment the supply of reclaimed water: various stormwater ponds within the city, including Ponds 46, 44, Gateway Activity Center, Weathersfield, Cranes Roost, and the wastewater treatment facility site.

Potable water may also be used to augment the supply of reclaimed water, subject to the requirements of the City’s cross connection control program.

Reclaimed water from the Apopka WWTF, upon execution of the reuse agreement, and the Wekiva Hunt Club WWTF, via interconnects with the reclaimed water transmission system, for irrigation at public access reuse sites, under a reclaimed water reuse agreement.

IN ACCORDANCE WITH: The limitations, monitoring requirements and other conditions set forth in Pages 1 through 22 of this permit.

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.
Surface Water Discharges

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to discharge effluent from Outfall D-001 to Little Wekiva River (Class III). Such discharge shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

	 
	
	
	Effluent Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (total to surface waters)
	MGD
	Maximum
	12.5
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-5
	See Cond. I.A.4.

	BOD, Carbonaceous 5 day, 20C
	mg/L
	Maximum
	5.0
	5.0
	7.5
	10.0
	5 Days/Week
	24-hour flow proportioned composite
	EFD-1
	

	Solids, Total Suspended
	mg/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	5 Days/Week
	24-hour flow proportioned composite
	EFD-1
	

	Coliform, Fecal
	#/100 ML
	Maximum
	See Permit Condition I.A.5.
	5 Days/Week
	Grab
	EFD-1
	

	pH
	SU
	Range
	-
	-
	-
	6.0-7.5
	Continuous
	Analyzer
	EFD-1
	See Cond. I.A.3.

	Total Residual Chlorine (For Disinfection)
	mg/L
	Minimum
	-
	-
	-
	0.5
	Continuous
	Analyzer
	EFA-1
	See Cond. I.A.3., 6.

	Total Residual Chlorine (For Dechlorination)
	mg/L
	Maximum
	-
	-
	-
	0.01
	Daily
	Grab
	EFD-1
	

	Nitrogen, Ammonia, Total as NH4
	mg/L AS NH4
	Maximum
	-
	1.0
	-
	-
	Daily
	24-hour flow proportioned composite
	EFD-1
	

	Phosphorus, Total  (as P)
	mg/L
	Maximum
	-
	Report
	-
	
	Weekly
	24-hour flow proportioned composite
	EFD-1
	

	Oxygen, Dissolved (DO)
	mg/L
	Minimum
	-
	-
	-
	6.0
	Daily
	Grab
	EFD-1
	

	Cadmium, Total Recoverable
	ug/L
	Maximum
	-
	-
	-
	Cond I.A.8
	Monthly
	Grab
	EFD-1
	

	Selenium, Total Recoverable
	ug/L
	Maximum
	-
	-
	-
	5.0
	Monthly
	Grab
	EFD-1
	

	Silver, Total Recoverable
	ug/L
	Maximum
	-
	-
	-
	0.07
	Monthly
	Grab
	EFD-1
	See Cond. I.A.9.

	Zinc, Total Recoverable
	ug/L
	Maximum
	-
	-
	-
	See Condition I.A.8
	Monthly
	Grab
	EFD-1
	See Cond. I.A.9.

	Dichlorobromomethane
	ug/L
	Maximum
	22
	-
	-
	
	Monthly
	Grab
	EFD-1
	See Cond. I.A.9.

	Whole Effluent Toxicity (Acute)
	See Permit Condition I.A.7.


	-
	


2. Effluent samples shall be taken at the monitoring site locations listed in Permit Condition I. A.  1. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-1
	Discharge from chlorine contact chamber

	EFD-1
	Discharge from neutralization tank

	FLW-5
	Ultrasonic flow meter at influent pipe to neutralization tank


3. Hourly measurement of pH and total residual chlorine for disinfection during the period of required operator attendance may be substituted for continuous measurement. [Chapter 62-601, Figure 2]
4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually. [62-601.200(17) and .500(6)]
5. The arithmetic mean of the monthly fecal coliform values collected during an annual period shall not exceed 200 per 100 mL of effluent sample.  The geometric mean of the fecal coliform values for a minimum of 10 samples of effluent each collected on a separate day during a period of 30 consecutive days (monthly), shall not exceed 200 per 100 mL of sample.  No more than 10 percent of the samples collected (the 90th percentile value) during a period of 30 consecutive days shall exceed 400 fecal coliform values per 100 mL of sample.  Any one sample shall not exceed 800 fecal coliform values per 100 mL of sample. Note: To report the 90th percentile value, list the fecal coliform values obtained during the month in ascending order. Report the value of the sample that corresponds to the 90th percentile (multiply the number of samples by 0.9).  For example, for 30 samples, report the corresponding fecal coliform number for the 27th value of ascending order.  [62-600.440(4)(c), 12-24-96]
6. A minimum of 0.5 mg/L total residual chlorine must be maintained for a minimum contact time of 15 minutes based on peak hourly flow. [62-600.440(5)(b) and (6)(b)]
7. The permittee shall continue the series of tests described below, to evaluate whole effluent toxicity of the discharge from outfall D001.

a. Effluent limitation

(1) Mortality of less than or equal to 20% in the 100% effluent concentration in any “routine” test shall constitute compliance with these permit conditions and Rule 62-303.200(1) and Rule 62-302.500(1)(a)4, F.A.C.  Mortality greater than 20% in the 100% effluent concentration in any test shall constitute unacceptable toxicity.  

(2) Whole effluent acute toxicity shall not exceed in any “routine” or in any “additional follow-up” test an LC50 of less than 100% effluent. [Rule 62-302.200(1), Rule 62-302.500(1)(a)4., and Rule 62-4.244(3)(a), F.A.C.]

b. Monitoring frequency

(1) “Routine” toxicity tests shall be conducted annually, during the annual “reclaimed holiday” in November/December of each year. 

c. Test Requirements:

(1) Routine Tests: All routine tests shall be conducted using a control (0% effluent) and a minimum of five dilutions: 100%, 50%, 25%, 12.5% and 6.25% effluent 

(2) The permittee shall conduct 96-hour acute static renewal multi-concentration toxicity tests using the daphnid, Ceriodaphnia dubia, and the bannerfin shiner, Cyprinella leedsi, concurrently.

(3) All test species, procedures and quality assurance criteria used shall be in accordance with Methods for Measuring Acute Toxicity of Effluents and Receiving Waters to Freshwater and Marine Organisms, EPA-821-R-02-012.  Any deviation of the bioassay procedures outlined herein shall be submitted in writing to the Department for review and approval prior to use.  In the event the above method is revised, the permittee shall conduct acute toxicity testing in accordance with the revised method.

(4) The control water and dilution water used will be moderately hard water as described in EPA-821-R-02-012, Table 7. 

d. Sampling Requirements

(1) Routine tests shall be conducted on four separate grab samples collected at evenly-spaced (6-hr) intervals over a 24-hour period and used in four separate tests in order to catch any peaks of toxicity and to account for daily variations in effluent quality.  Companion chemistries will be collected at the time of toxicity testing sampling, but should be run only in the event of a test failure except that the permittee shall analyze at sample collection time any parameters such as unionized ammonia that have a short holding time and whose results would be adversely affected by preservation and length of holding times.  

(2) If unacceptable acute toxicity is found in a “routine” test, the permittee shall conduct the following analytical chemistry analyses on the chemistry sample taken at the time of the bioassay sample: Pesticides & Herbicides, Metals, Unionized Ammonia, pH, Dissolved Oxygen, Conductivity and Nutrients. Upon completion of the analytical chemistries, the permittee shall submit all results, in a report prepared according to EPA-821-R-02-012, Section 12, Report Preparation and Test Review and mailed to the Department at the address below within 45 days of the completion of the “routine” test.  Additionally, the permittee will meet with the Department, after a single test failure, to discuss corrective action necessary to remedy the observed toxicity violation.  

e. Quality Assurance Requirements

(1) A standard reference toxicant (SRT) quality assurance (QA) acute toxicity test shall be conducted with each species used in the required toxicity tests either concurrently or started no more than 30 days before the date of each routine or additional follow-up test conducted.  The SRT-QA data shall be submitted with each companion routine or additional follow-up test required.

(2) If the mortality in the control (0% effluent) exceeds 10% for either species in any test, the test for that species (including the control) shall be invalidated and the test repeated. 

(3) If during any routine separate grab sample test, 100% mortality occurs prior to the end of the test and control mortality is less than 10% at that time, that test (including the control) shall be terminated with the conclusion that the test fails and constitutes non-compliance.

f. Reporting Requirements

(1) Results from all required tests shall be reported on the Discharge Monitoring Report (DMR) as follows:  If an LC50> 100% effluent occurs in all four separate grab sample tests for the test species, “>100%” should be entered on the DMR for that test species. If in any of the four separate grab sample tests for the test species a LC50 < 100% effluent occurs, the lowest calculated LC50 effluent concentration shall be entered on the DMR for that test species. 

(2) A bioassay laboratory report for the routine test shall be prepared according to EPA-821-R-02-012, Section 12, Report Preparation and Test Review and mailed to the Department at the address below within 30 days of the completion of the test. 

(3) All bioassay reports shall be submitted to:

Florida Department of Environmental Protection

Central District Office

3319 Maguire Boulevard, Suite 232

Orlando, FL 32803-3767 

8. The limit for “Cadmium, Total Recoverable” shall be calculated using the following equation:

Cd   e^(0.7409[lnH]-4.791)

The limit for “Zinc, Total Recoverable” shall be calculated using the following equation

Zn ( e^ (0.8473[lnH]+0.884)

Total hardness shall be measured at the time of the effluent sample.  The “ln H” means the natural logarithm of total hardness expressed as mg/L of CaCO3.  For metals criteria involving equations with hardness, the hardness shall be set at 25 mg/L if actual hardness is <25 mg/L and set at 400 mg/L if actual hardness is >400 mg/L.

The measured effluent value shall be recorded on the DMR in the parameter row for “effluent.”  The calculated effluent limit shall be recorded on the DMR in the parameter row for “calculated limit.”  Compliance with the effluent limitation is determined by calculating the difference between the measured effluent value and the calculated.  The compliance value shall be recorded on the DMR in the parameter row for “effluent minus calculated limit.”  If the compliance value is greater than 0.00, the permittee will be considered in violation of the limitation.  [ 62-302.530(15)]
9. The permittee will monitor silver, zinc, cadmium and dichlorobromomethane monthly (during months in which a surface water discharge occurs) until a minimum of twelve samples are obtained.  The results of these analyses shall be used to determine if there is reasonable assurance that these constituents will not exceed the surface water quality standards for these parameters. The Department shall reserve the right to revise this permit to incorporate additional monitoring or effluent limits or to relieve the permittee of the monitoring requirements. [62-302]
10. The Department may develop a Total Maximum Daily Load (TMDL) for this section of the Little Wekiva River during the life of this permit.  Once a TMDL for this water body has been established and adopted by rule, the Department shall revise this permit to incorporate the final findings of the TMDL, pursuant to Rule 62-620.325, Florida Administrative Code.  This may also include limits for coliform and nutrients, which are listed as parameters of concern on the 303d list for the Wekiva River.”
11. In addition to the specified limits, the monthly average effluent concentration for total suspended solids shall not exceed 15% of the respective influent value (i.e., 85% removal).

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

B.
Reuse and Land Application Systems

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to supplement reclaimed water with surface water and ground water and direct reclaimed water to Reuse System R-001.  Such reclaimed water shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

	 
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (effluent to public access irrigation system)
	MGD
	Maximum
	12.5
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-2
	See Cond. I.B.4.

	Flow (ground water to public access irrigation system)
	MGD
	Maximum
	Report
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-3
	See Cond. I.B.4.

	Flow (surface water to public access irrigation system)
	MGD
	Maximum
	1.5
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-4
	See Cond. I.B.4.

	BOD, Carbonaceous 5 day, 20C
	mg/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	4 Days/Week
	24-hour flow proportioned composite
	EFA-1
	

	Solids, Total Suspended
	mg/L
	Maximum
	-
	-
	-
	5.0
	4 Days/Week
	Grab
	EFB-1
	

	pH
	SU
	Range
	-
	-
	-
	6.0 to 8.5
	Continuous
	Meter
	EFA-1
	See Cond. I.B.3.

	Coliform, Fecal
	#/100 ML
	Maximum
	See Permit Condition I.B.5.
	4 Days/Week
	Grab
	EFA-1
	

	Total Residual Chlorine (For Disinfection)
	mg/L
	Minimum
	-
	-
	-
	1.0
	Continuous
	Meter
	EFA-1
	See Cond. I.B.6.

	Turbidity
	NTU
	Maximum
	See Permit Condition I.B.7.
	Continuous
	Meter
	EFB-1
	

	Giardia
	CYSTS/ 100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-1
	

	Cryptosporidium
	OOCYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-1
	

	Coliform, Fecal
	#/100 ML
	Maximum
	
	
	
	Report
	Annually
	Grab
	OTH-1
	


2. Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I. B.  1. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-1
	Discharge from chlorine contact chamber

	EFB-1
	Discharge from reaeration tank (prior to chlorination)

	FLW-2
	Ultrasonic flow meter at discharge from chlorine contact chamber

	FLW-3
	Supplemental groundwater supply well flows

	FLW-4
	Supplemental surface water flows

	OTH-1
	supplemental ground water supply after chlorination


3. Hourly measurement of pH during the period of required operator attendance may be substituted for continuous measurement.  [Chapter 62-601, Figure 2]  

4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.  Note:  To report the “% less than detection,” count the number of fecal coliform observations that were less than detection, divide by the total number of fecal coliform observations in the month, and multiply by 100% (round to the nearest integer).  [62-600.440(5)(f)]  

6. The minimum total chlorine residual shall be limited as described in the approved operating protocol, such that the permit limitation for fecal coliform bacteria will be achieved.  In no case shall the total chlorine residual be less than 1.0 mg/L.  [62-600.440(5)(b); 62-610.460(2); and 62-610.463(2)]  

7. The maximum turbidity shall be limited as described in the approved operating protocol, such that the permit limitations for total suspended solids and fecal coliforms will be achieved.  [62-610.463(2)]  

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

C.
Other Limitations and Monitoring and Reporting Requirements

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the treatment facility shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.C.11:

	
	
	
	Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (total through treatment plant)
	MGD
	Maximum
	12.5
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-1
	See Cond. I.C.4.

	Solids, Total Suspended
	mg/L
	Maximum
	-
	Report
	-
	-
	5 Days/Week
	24-hour flow proportioned composite
	INF-2
	See Cond. I.C.3.

	BOD, Carbonaceous 5 day, 20C
	mg/L
	Maximum
	-
	Report
	-
	-
	5 Days/Week
	24-hour flow proportioned composite
	INF-2
	See Cond. I.C.3.

	Percent Capacity, (TMADF/Permitted Capacity) x 100
	Percent
	Maximum
	-
	Report
	-
	-
	Monthly
	Calculated
	CAL-1
	


2. Samples shall be taken at the monitoring site locations listed in Permit Condition I. C. 1 and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	INF-2
	Automatic sampler at headworks

	FLW-1
	Ultrasonic flow meter at parshall flume

	CAL-1
	Calculated using FLW-1


3. Influent samples shall be collected so that they do not contain digester supernatant or return activated sludge, or any other plant process recycled waters. [62-601.500(4)]
4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. The treatment facilities shall be operated in accordance with all approved operating protocols.  Only reclaimed water that meets the criteria established in the approved operating protocol(s) may be released to system storage or to the reuse system.  Reclaimed water that fails to meet the criteria in the approved operating protocol(s) shall be directed to the following permitted alternate discharge system: An existing 12.5 mgd AADF permitted discharge to Little Wekiva River at the outfall, Discharge Location (D-001),. The operating protocol(s) shall be reviewed and updated periodically to ensure continuous compliance with the minimum treatment and disinfection requirements.  Updated operating protocols shall be submitted to the Department for review and approval upon revision of the operating protocol(s) and with each permit application.  [62-610.320(6) and 62-610.463(2)]  

6. Instruments for continuous on-line monitoring of total residual chlorine and turbidity shall be equipped with an automated data logging or recording device.  [62-610.463(2) & .865(8)(d)]
7. Intervals between sampling for Giardia and Cryptosporidium shall not exceed two years.  Sampling results shall be reported on DEP Form 62-610.300(4)(a)4 which is attached to this permit.  This form shall be submitted to the Department and to DEP’s Reuse Coordinator in Tallahassee.  [62-610.463(4) and .472(3)(d)]
8. Parameters which must be monitored as a result of a surface water discharge shall be analyzed using a sufficiently sensitive method to assure compliance with applicable water quality standards and effluent limitations in accordance with 40 CFR (Code of Federal Regulations) Part 136.  All monitoring shall be representative of the monitored activity. [62-620.320(6)]
9. The sample collection, analytical test methods and method detection limits (MDLs) applicable to this permit shall be in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.  The list of Department established analytical methods, and corresponding MDLs (method detection limits) and PQLs (practical quantitation limits), which is titled “Florida Department of Environmental Protection Table as Required By Rule 62-4.246(4) Testing Methods for Discharges to Surface Water” is available at http://www.dep.state.fl.us/labs/guidance/index.htm.  The MDLs and PQLs as described in this list shall constitute the minimum acceptable MDL/PQL values and the Department shall not accept results for which the laboratory's MDLs or PQLs are greater than those described above unless alternate MDLs and/or PQLs have been specifically approved by the Department for this permit. Any method included in the list may be used for reporting as long as it meets the following requirements: 

a)
The laboratory’s reported MDL and PQL values for the particular method must be equal or less than the corresponding method values specified in the Department’s approved MDL and PQL list;

b)
The laboratory reported MDL for the specific parameter is less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Parameters that are listed as “report only” in the permit shall use methods that provide a MDL, which is equal to or less than the applicable water quality criteria stated in 62-302, F.A.C.; and

c)
If the MDLs for all methods available in the approved list are above the stated permit limit or applicable water quality criteria for that parameter, then the method with the lowest stated MDL shall be used.

Where necessary, the permittee may request approval of alternate methods or for alternative MDLs or PQLs for any approved analytical method.  Approval of alternate laboratory MDLs or PQLs are not necessary if the laboratory reported MDLs and PQLs are less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Approval of an analytical method not included in the above-referenced list is not necessary if the analytical method is in accordance with 40 CFR 136.   [62-4.246, 62-160] 

10. The permittee shall provide safe access points for obtaining representative influent, reclaimed water, and effluent samples which are required by this permit. [62-601.500(5)]
11. Monitoring requirements under this permit are effective on the first day of the second month following permit issuance.  Until such time, the permittee shall continue to monitor and report in accordance with previously effective permit requirements, if any.  During the period of operation authorized by this permit, the permittee shall complete and submit to the Department Discharge Monitoring Reports (DMRs) in accordance with the frequencies specified by the REPORT type (i.e., monthly, toxicity, quarterly, semiannual, annual, etc.) indicated on the DMR forms attached to this permit.  Monitoring results for each monitoring period shall be submitted in accordance with the associated DMR due dates below.  

	REPORT Type
	Monitoring Period
	Due Date

	Monthly or Toxicity
	first day of month – last day of month
	28th day of following month

	Quarterly
	January 1 - March 31
April 1 – June 30
July 1 – September 30 
October 1 – December 31 
	April 28
July 28
October 28
January 28

	Semiannual
	January 1 – June 30
July 1 – December 31 
	July 28
January 28

	Annual
	January 1 – December 31
	January 28 


DMRs shall be submitted for each required monitoring period including months of no discharge.  The permittee shall make copies of the attached DMR form(s) and shall submit the completed DMR form(s) to the Department by the twenty-eighth (28th) of the month following the month of operation at the address specified below: 

Florida Department of Environmental Protection

Wastewater Compliance Evaluation Section, Mail Station 3551

Twin Towers Office Building

2600 Blair Stone Road

Tallahassee, Florida 32399-2400

[62-620.610(18)][62-601.300(1),(2), and (3)]
12. During the period of operation authorized by this permit, reclaimed water or effluent shall be monitored annually for the primary and secondary drinking water standards contained in Chapter 62-550, F.A.C., (except for asbestos, color, and corrosivity). Twenty-four hour composite samples shall be used to analyze reclaimed water or effluent for the primary and secondary drinking water standards. These monitoring results shall be reported to the Department’s Central District Office annually on the DMR. During years when a permit is not renewed, a certification stating that no new non-domestic wastewater dischargers have been added to the collection system since the last reclaimed water or effluent analysis was conducted may be submitted in lieu of the report. The annual reclaimed water or effluent analysis report or the certification shall be completed and submitted in a timely manner so as to be received by the Department’s Central District Office by June 28 of each year.  Approved analytical methods identified in Rule 62-620.100(3)(i), F.A.C., shall be used for the analysis.  If no method is included for a parameter, methods specified in Chapter 62-550, F.A.C., shall be used.  [62-601.300(4)][62-601.500(3)][62-610.300(4)]
13. The permittee shall submit an Annual Reuse Report using DEP Form 62-610.300(4)(a)2. on or before January 1 of each year.  [62-610.870(3)]
14. The permittee shall maintain an inventory of storage systems.  The inventory shall be submitted to the Department at least 30 days before reclaimed water will be introduced into any new storage system.  The inventory of storage systems shall be attached to the annual submittal of the Annual Reuse Report.  [62-610.464(5)]
15. Unless specified otherwise in this permit, all reports and other information required by this permit, including 24-hour notifications, shall be submitted to or reported to, as appropriate, the Department's Central District Office at the address specified below:

Central District Office

3319 Maguire Boulevard Suite 232
Orlando, Florida 32803-3767

Phone Number - (407) 894-7555

FAX Number -  (407) 897-2966   

All FAX copies shall be followed by original copies.  All reports and other information shall be signed in accordance with the requirements of Rule 62-620.305, F.A.C.  [62-620.305]
II.
RESIDUALS MANAGEMENT REQUIREMENTS 

1.  The method of residuals use or disposal by this facility is transport to Florida N-Viro/Tomoka Farms Residuals Management Facility or disposal in a Class I or II solid waste landfill.

2.  The permittee shall be responsible for proper treatment, management, use, and land application or disposal of its residuals.  [62-640.300(5)]
3. The permittee shall not be held responsible for treatment, management, use, or land application violations that occur after its residuals have been accepted by a permitted residuals management facility with which the source facility has an agreement in accordance with Rule 62-640.880(1)(c), F.A.C., for further treatment, management, use or land application.  [62-640.300(5)]
4. Disposal of residuals, septage, and other solids in a solid waste landfill, or disposal by placement on land for purposes other than soil conditioning or fertilization, such as at a monofill, surface impoundment, waste pile, or dedicated site, shall be in accordance with Chapter 62-701, F.A.C.  [62-640.100(6)(k)3 & 4]  

5. If the permittee intends to accept residuals from other facilities, a permit revision is required pursuant to Rule 62-640.880(2)(d), F.A.C. [62-640.880(2)(d)]  

6. The permittee shall keep hauling records to track the transport of residuals between facilities.  The hauling records shall contain the following information:  

	Source Facility
	Residuals Management Facility or Treatment Facility

	1.
Date and Time Shipped
	1.
Date and Time Received

	2.
Amount of Residuals Shipped
	2.
Amount of Residuals Received

	3.
Degree of Treatment (if applicable)
	3.
Name and ID Number of Source Facility

	4.
Name and ID Number of Residuals 
	4.
Signature of Hauler

	
Management Facility or Treatment Facility
	5.
Signature of Responsible Party at Residuals Management Facility or Treatment Facility

	5. 
Signature of Responsible Party at Source Facility
	

	6. 
Signature of Hauler and Name of Hauling Firm
	


These records shall be kept for five years and shall be made available for inspection upon request by the Department.  A copy of the hauling records information maintained by the source facility shall be provided upon delivery of the residuals to the residuals management facility or treatment facility.  The permittee shall report to the Department within 24 hours of discovery any discrepancy in the quantity of residuals leaving the source facility and arriving at the residuals management facility or treatment facility.  [62-640.880(4)]  

7. Storage of residuals or other solids at the permitted facility shall require prior written notification to the Department.  [62-640.300(4)]  

III.
GROUND WATER REQUIREMENTS

Section III is not applicable to this facility.

IV.
ADDITIONAL REUSE AND LAND APPLICATION REQUIREMENTS

Part III Public Access System(s) (R-001)
1. Use of reclaimed water is authorized within the general service area identified in the attached map.  The following uses of reclaimed water are authorized within this general service area:  Athletic Complexes and Parks, Business, Commercial and Industrial Parks, Golf Courses, Industrial and Manufacturing Facilities, Residential Developments, Landscape areas, Highway medians, right of ways, Car wash, toilet flushing, cooling towers and phasing out fire hydrants.  [62-620.630(10)(d)]
2. New major users of reclaimed water (i.e., using 0.1 MGD or more) may be added to the reuse system using the general permit described in Rule 62-610.890, F.A.C., if the requirements in this rule are complied with.  Application for use of this general permit shall be made using Form 62-610.300(4)(a)1.  [62-610.890]
3. Cross-connections to the potable water system are prohibited.  [62-610.469(7)]
4. A cross-connection control program shall be implemented and/or remain in effect within the areas where reclaimed water will be provided for use.  [62-610.469(7)]
5. The permittee shall conduct inspections within the reclaimed water service area to verify proper connections, to minimize illegal cross-connections, and to verify the proper use of reclaimed water.  Inspections are required when a customer first connects to the reuse distribution system.  Subsequent inspections are required as specified in the cross-connection control and inspection program.  [62-610.469(7)(h)]
6. If a cross-connection between the potable and reclaimed water systems is discovered, the permittee shall:

a.
Immediately discontinue potable water and/or reclaimed water service to the affected area.

b.
If the potable water system is contaminated, clear the potable water lines.

c.
Eliminate the cross-connection.

d.
Test the affected area for other possible cross-connections.

e.
Within 24 hours, notify the Central District Office's domestic wastewater and drinking water programs.

f.
Within 5 days of discovery of a cross-connection, submit a written report to the Department detailing: a description of the cross-connection, how the cross-connection was discovered, the exact date and time of discovery, approximate time that the cross-connection existed, the location, the cause, steps taken to eliminate the cross-connection, whether reclaimed water was consumed, and reports of possible illness, whether the drinking water system was contaminated and the steps taken to clear the drinking water system, when the cross-connection was eliminated, plan of action for testing for other possible cross-connections in the area, and an evaluation of the cross-connection control and inspection program to ensure that future cross-connections do not occur.  [62-555.350(3) and 62-555.360][62-620.610(20)]
7. Maximum obtainable separation of reclaimed water lines and potable water lines shall be provided and the minimum separation distances specified in Rule 62-610.469(7), F.A.C., shall be provided.  Reuse facilities shall be color coded or marked.  Underground piping which is not manufactured of metal or concrete shall be color-coded using Pantone Purple 522C using light stable colorants.  Underground metal and concrete pipe shall be color-coded or marked using purple as the predominant color.  [62-610.469(7)]
8. In constructing reclaimed water distribution piping, the permittee shall maintain a 75-foot setback distance from a reclaimed water transmission facility to public water supply wells.  No setback distances are required to other potable water supply wells or to any nonpotable water supply wells.  [62-610.471(3)]
9. A setback distance of 75 feet shall be maintained between the edge of the wetted area and potable water supply wells, unless the utility adopts and enforces an ordinance prohibiting potable water supply wells within the reuse service area.  No setback distances are required to any nonpotable water supply well, to any surface water,  to any developed areas, or to any private swimming pools, hot tubs, spas, saunas, picnic tables, barbecue pits, or barbecue grills.  [62-610.471(1), (2), (5), and (7)]
10. Reclaimed water shall not be used to fill swimming pools, hot tubs, or wading pools.  [62-610.469(4)]
11. Low trajectory nozzles, or other means to minimize aerosol formation shall be used within 100 feet from outdoor public eating, drinking, or bathing facilities.  [62-610.471(6)]
12. A setback distance of 100 feet shall be maintained from indoor aesthetic features using reclaimed water to adjacent indoor public eating and drinking facilities.  [62-610.471(8)]
13. The public shall be notified of the use of reclaimed water.  This shall be accomplished by posting of advisory signs in areas where reuse is practiced, notes on scorecards, or other methods.  [62-610.468(2)]
14. All new advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets shall bear the words “do not drink” and “no beber” along with the equivalent standard international symbol.  In addition to the words “do not drink” and “no beber,” advisory signs posted at storage ponds and decorative water features shall also bear the words “do not swim” and “no nadar” along with the equivalent standard international symbols.  If any existing advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets are found, that do not have the new language the permittee shall be replaced with the above language within ten days.  [62-610.468 & 62-610.469]
15. The permittee shall ensure that users of reclaimed water are informed about the origin, nature, and characteristics of reclaimed water; the manner in which reclaimed water can be safely used; and limitations on the use of reclaimed water. Notification is required at the time of initial connection to the reclaimed water distribution system and annually after the reuse system is placed into operation.  A description of on-going public notification activities shall be included in the Annual Reuse Report.  [62-610.468(6)]
16. Routine aquatic weed control and regular maintenance of storage pond embankments and access areas are required.  [62-610.414 & 62-610.464]
17. Overflows from emergency discharge facilities on storage ponds shall be reported as an abnormal event to the Department's Central District Office within 24 hours of an occurrence.  The provisions of Rule 62-610.800(9), F.A.C., shall be met.  [62-610.800(9)]
Supplemental Water Supplies – Surface Waters and Discharge of Stormwater into the Sewerage System
18. The mixture of reclaimed water and surface water shall not harm vegetation or crops grown in the reuse system.  [62-610.472(3)]
19. A one-way flow device shall be provided on each surface water supply line to prevent backflow of reclaimed water into the surface water or into the stormwater treatment facilities.  [62-610.472(3)]
20. The supplemental water supply pipes and appurtenances shall be color coded and marked to differentiate them from the reclaimed water and potable water facilities.  [62-610.472(3)]
21. Facilities used to connect supplemental water supplies into the reclaimed water distribution system shall be located and documented in the record drawings for the reuse system.  [62-610.472(7)]
Supplemental Water Supplies – Ground Water

22. An approved backflow prevention device, as described in Rule 62-555.360, F.A.C., shall be provided on the pipe from each well connected into the reclaimed water system.  [62-610.472(4)]
23. The supplemental water supply pipes and appurtenances shall be color coded and marked to differentiate them from the reclaimed water and potable water facilities.  [62-610.472(4)]
24. Facilities used to connect supplemental water supplies into the reclaimed water distribution system shall be located and documented in the record drawings for the reuse system.  [62-610.472(7)]
Supplemental Water Supplies – Discharge of Stormwater into the Sewerage System

25. Introduction of stormwater into the sewerage system shall be limited to dry-weather, low-flow conditions in the sanitary sewerage system. [62-610.472(3)(c)]
Cranes Roost Storage

26. The Cranes Roost storage pond, which is used periodically for recreational purposes, shall be used for reclaimed water storage as described in the approved protocol for use of the lake.

V.
OPERATION AND MAINTENANCE REQUIREMENTS

1.
During the period of operation authorized by this permit, the wastewater facilities shall be operated under the supervision of a(n) operator(s) certified in accordance with Chapter 62-602, F.A.C.  In accordance with Chapter 62-699, F.A.C., this facility is a Category I, Class A facility and, at a minimum, operators with appropriate certification must be on the site as follows:

A Class C or higher operator 24 hours/day for 7 days/week.  The lead operator must be a Class A.

[62-620.630(3)] [62-699.310] [62-610.462]
2. The lead operator shall be employed at the plant full time.  “Full time” shall mean at least 4 days per week, working a minimum of 35 hours per week, including leave time.  A certified operator shall be on-site and in charge of each required shift and for periods of required staffing time when the lead operator is not on-site.  An operator meeting the lead operator classification level of the plant shall be available during all periods of plant operation.  “Available” means able to be contacted as needed to initiate the appropriate action in a timely manner.  [62-699.311(10), (5) and (1)]
3. The application to renew this permit shall include an updated capacity analysis report prepared in accordance with Rule 62-600.405, F.A.C.  [62-600.405(5)]
4. The application to renew this permit shall include a detailed operation and maintenance performance report prepared in accordance with Rule 62-600.735, F.A.C.  [62-600.735(1)]
5. The permittee shall maintain the following records and make them available for inspection on the site of the permitted facility:

a.
Records of all compliance monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation and a copy of the laboratory certification showing the certification number of the laboratory, for at least three years from the date the sample or measurement was taken;

b.
Copies of all reports required by the permit for at least three years from the date the report was prepared;

c.
Records of all data, including reports and documents, used to complete the application for the permit for at least three years from the date the application was filed;

d.
Monitoring information, including a copy of the laboratory certification showing the laboratory certification number, related to the residuals use and disposal activities for the time period set forth in Chapter 62-640, F.A.C., for at least three years from the date of sampling or measurement;

e.
A copy of the current permit;

f.
A copy of the current operation and maintenance manual as required by Chapter 62-600,. F.A.C.;

g.
A copy of the facility record drawings;

h.
Copies of the licenses of the current certified operators; and 

i.
Copies of the logs and schedules showing plant operations and equipment maintenance for three years from the date of the logs or schedules.  The logs shall, at a minimum, include identification of the plant; the signature and certification number of the operator(s) and the signature of the person(s) making any entries; date and time in and out; specific operation and maintenance activities; tests performed and samples taken; and major repairs made. The logs shall be maintained on-site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed.


[62-620.350]
VI.
SCHEDULES

1. In accordance with Rule 62-600.550, F.A.C., a permit revision will be required in order to comply with the Wekiva wastewater rules by April 12, 2011.  [62-600.550]
2. In accordance with sections 403.088(2)(e) and (f), Florida Statutes, a compliance schedule for this facility is contained in Administrative Order 06-2162 which is hereby incorporated by reference.

VII.  INDUSTRIAL PRETREATMENT PROGRAM REQUIREMENTS

1. The permittee shall function as the Control Authority and shall be responsible for the performance of all pretreatment program requirements contained in Chapter 62-625, F.A.C.  The permittee shall be subject to enforcement actions, penalties, and other remedies by the Department or other appropriate parties.  The permittee shall implement and enforce its Approved Pretreatment Program.  The permittee's Approved Pretreatment Program is hereby made an enforceable condition of this permit.  The Department may initiate enforcement action against an industrial user for noncompliance with applicable standards and requirements. [62-625.500]
2. The permittee shall enforce the requirements promulgated under Sections 307(b), 307(c), 307(d), and 402(b) of the Act.  The permittee shall cause industrial users subject to Federal Categorical Standards to achieve compliance no later than the date specified in those requirements or, in the case of new industrial users, upon commencement of the discharge. [62-625.410]
3. The permittee shall perform the pretreatment functions as required in Chapter 62-625, F.A.C., including, but not limited to, the following:

a.
Implementing the necessary legal authorities as provided in Rule 62-625.500(2)(a), F.A.C.  This includes, among other things, the authority to require compliance with applicable pretreatment standards, which includes general prohibitions listed in Rule 62-625.400(1), F.A.C., specific prohibitions in Rule 62-625.400(2), F.A.C., locally developed limits as required by Rules 62-625.400(3) and (4), F.A.C., and national categorical limits in accordance with Rule 62-625.410, F.A.C.; 

b.
Implementing the programmatic functions as required under Rule 62-625.500(2)(b), F.A.C.; 

c.
Providing the required funding, equipment, and personnel to implement the pretreatment program as provided in Rules 62-625.500(2), (3), and (4), F.A.C.; and

d.
Providing a written technical evaluation that local limits have been developed in accordance with Rule 62-625.400(3)(a), F.A.C.  The evaluation shall verify whether existing local limits protect the wastewater facilities, and if not, the permittee shall develop new local limits as part of the evaluation.  This evaluation shall be submitted to the Department at the address in the condition below within 180 days after permit renewal.  

[62-625.400 and .500]
4. As required by Rules 62-625.600(8) and (12), F.A.C., the permittee shall submit a signed copy of the annual report for pretreatment activities, including DMRs for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R, to the Department at the following address:

Florida Department of Environmental Protection

Domestic Wastewater Section, Mail Station 3540

Twin Towers Office Building

2600 Blair Stone Road

Tallahassee, Florida 32399-2400


The annual report shall contain the information required in accordance with Rule 62‑625.600(8), F.A.C., except section (8)(e) as noted below, and shall describe the permittee's pretreatment activities for the reporting year.  In the event that the permittee is not in compliance with any conditions or requirements of the pretreatment program, then the permittee shall also include the reasons for noncompliance and state how and when the permittee shall comply with such conditions and requirements.  


In order to comply with Rule 62-625.600(8)(e), F.A.C., the permittee shall submit annual DMRs with the analytical results of influent, effluent, and residuals for those pollutants listed on the DMRs.  For any other nonpriority pollutants which the permittee believes may be causing or contributing to interference, pass through, or adversely impacting residuals quality, the annual report shall provide a summary of all analytical results of influent, effluent, and residuals.  The annual report and DMRs are due on November 1 of each year.


[62-625.600(12)]
5. Samples for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R shall be taken at the monitoring site locations described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	PRT-I
	prior to the parshall flume (INF-2)

	PRT-E
	Discharge from chlorine contact chamber

	PRT-R
	Final residuals from digester


VIII.  OTHER SPECIFIC CONDITIONS

1. The permittee shall apply for renewal of this permit at least 180 days before the expiration date of the permit using the appropriate forms listed in Rule 62-620.910, F.A.C., including submittal of the appropriate processing fee set forth in Rule 62-4.050, F.A.C.  The existing permit shall not expire until the Department has taken final action on the application renewal in accordance with the provisions of 62-620.335(3) and (4), F.A.C.  [62-620.335(1)-(4)]
2. Florida water quality criteria and standards shall not be violated as a result of any discharge or land application of reclaimed water or residuals from this facility.  [62-620.320(9) and 62-302.500(2)(e)][62-610.850(1)(a) and (2)(a)]
3. In the event that the treatment facilities or equipment no longer function as intended, are no longer safe in terms of public health and safety, or odor, noise, aerosol drift, or lighting adversely affects neighboring developed areas at the levels prohibited by Rule 62-600.400(2)(a), F.A.C., corrective action (which may include additional maintenance or modifications of the permitted facilities) shall be taken by the permittee.  Other corrective action may be required to ensure compliance with rules of the Department.  Additionally, the treatment, management, use or land application of residuals shall not cause a violation of the odor prohibition in Rule 62-296.320(2), F.A.C.  [62-600.410(8) and 62-640.400(6)]
4. The deliberate introduction of stormwater in any amount into collection/transmission systems designed solely for the introduction (and conveyance) of domestic/industrial wastewater; or the deliberate introduction of stormwater into collection/transmission systems designed for the introduction or conveyance of combinations of storm and domestic/industrial wastewater in amounts which may reduce the efficiency of pollutant removal by the treatment plant is prohibited, except as provided by Rule 62-610.472, F.A.C.  [62-604.130(3)]
5. Collection/transmission system overflows shall be reported to the Department in accordance with Permit Condition IX. 20.  [62-604.550]  [62-620.610(20)]
6. The operating authority of a collection/transmission system and the permittee of a treatment plant are prohibited from accepting connections of wastewater discharges which have not received necessary pretreatment or which contain materials or pollutants (other than normal domestic wastewater constituents):

a.
Which may cause fire or explosion hazards; or

b.
Which may cause excessive corrosion or other deterioration of wastewater facilities due to chemical action or pH levels; or

c.
Which are solid or viscous and obstruct flow or otherwise interfere with wastewater facility operations or treatment; or

d.
Which result in the wastewater temperature at the introduction of the treatment plant exceeding 40oC or otherwise inhibiting treatment; or

e.
Which result in the presence of toxic gases, vapors, or fumes that may cause worker health or safety problems.

[62-604.130(5)]
7. The treatment facility, storage ponds, rapid infiltration basins, and/or infiltration trenches shall be enclosed with a fence or otherwise provided with features to discourage the entry of animals and unauthorized persons.  [62-600.400(2)(b)] 
8. Screenings and grit removed from the wastewater facilities shall be collected in suitable containers and hauled to a Department approved Class I landfill or to a landfill approved by the Department for receipt/disposal of screenings and grit.  [62-701.300(1)(a)]
9. The Permittee shall provide verbal notice to the Department as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The Permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department in a written report within 7 days of the sinkhole discovery.  [62-4.070(3)]
IX.
GENERAL CONDITIONS

1.
The terms, conditions, requirements, limitations and restrictions set forth in this permit are binding and enforceable pursuant to Chapter 403, Florida Statutes.  Any permit noncompliance constitutes a violation of Chapter 403, Florida Statutes, and is grounds for enforcement action, permit termination, permit revocation and reissuance, or permit revision.  [62-620.610(1)]

2.
This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviations from the approved drawings, exhibits, specifications or conditions of this permit constitutes grounds for revocation and enforcement action by the Department.  [62-620.610(2)]
3.
As provided in subsection 403.087(7), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor authorize any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit or authorization that may be required for other aspects of the total project which are not addressed in this permit.  [62-620.610(3)]
4.
This permit conveys no title to land or water, does not constitute state recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [62-620.610(4)]

5.
This permit does not relieve the permittee from liability and penalties for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source; nor does it allow the permittee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department.  The permittee shall take all reasonable steps to minimize or prevent any discharge, reuse of reclaimed water, or residuals use or disposal in violation of this permit which has a reasonable likelihood of adversely affecting human health or the environment.  It shall not be a defense for a permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this permit.  [62-620.610(5)]
6.
If the permittee wishes to continue an activity regulated by this permit after its expiration date, the permittee shall apply for and obtain a new permit.  [62-620.610(6)]
7.
The permittee shall at all times properly operate and maintain the facility and systems of treatment and control, and related appurtenances, that are installed and used by the permittee to achieve compliance with the conditions of this permit.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to maintain or achieve compliance with the conditions of the permit.  [62-620.610(7)]

8.
This permit may be modified, revoked and reissued, or terminated for cause.  The filing of a request by the permittee for a permit revision, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition.  [62-620.610(8)]

9.
The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, including an authorized representative of the Department and authorized EPA personnel, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated, to:

a.
Enter upon the permittee’s premises where a regulated facility, system, or activity is located or conducted, or where records shall be kept under the conditions of this permit;

b.
Have access to and copy any records that shall be kept under the conditions of this permit;

c.
Inspect the facilities, equipment, practices, or operations regulated or required under this permit; and

d.
Sample or monitor any substances or parameters at any location necessary to assure compliance with this permit or Department rules.


[62-620.610(9)]

10.
In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data, and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except as such use is proscribed by Section 403.111, Florida Statutes, or Rule 62-620.302, Florida Administrative Code.  Such evidence shall only be used to the extent that it is consistent with the Florida Rules of Civil Procedure and applicable evidentiary rules.  [62-620.610(10)]

11.
When requested by the Department, the permittee shall within a reasonable time provide any information required by law which is needed to determine whether there is cause for revising, revoking and reissuing, or terminating this permit, or to determine compliance with the permit.  The permittee shall also provide to the Department upon request copies of records required by this permit to be kept.  If the permittee becomes aware of relevant facts that were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be promptly submitted or corrections promptly reported to the Department.  [62-620.610(11)]

12.
Unless specifically stated otherwise in Department rules, the permittee, in accepting this permit, agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.  A reasonable time for compliance with a new or amended surface water quality standard, other than those standards addressed in Rule 62-302.500, F.A.C., shall include a reasonable time to obtain or be denied a mixing zone for the new or amended standard.  [62-620.610(12)]

13.
The permittee, in accepting this permit, agrees to pay the applicable regulatory program and surveillance fee in accordance with Rule 62-4.052, F.A.C.  [62-620.610(13)]

14.
This permit is transferable only upon Department approval in accordance with Rule 62-620.340, F.A.C.  The permittee shall be liable for any noncompliance of the permitted activity until the transfer is approved by the Department.  [62-620.610(14)]

15.
The permittee shall give the Department written notice at least 60 days before inactivation or abandonment of a wastewater facility and shall specify what steps will be taken to safeguard public health and safety during and following inactivation or abandonment.  [62-620.610(15)]

16.
The permittee shall apply for a revision to the Department permit in accordance with Rules 62-620.300 and the Department of Environmental Protection Guide to Wastewater Permitting at least 90 days before construction of any planned substantial modifications to the permitted facility is to commence or with Rule 62-620.325(2) for minor modifications to the permitted facility.  A revised permit shall be obtained before construction begins except as provided in Rule 62-620.300, F.A.C.  [62-620.610(16)]
17.
The permittee shall give advance notice to the Department of any planned changes in the permitted facility or activity which may result in noncompliance with permit requirements.  The permittee shall be responsible for any and all damages which may result from the changes and may be subject to enforcement action by the Department for penalties or revocation of this permit.  The notice shall include the following information:

a.
A description of the anticipated noncompliance;

b.
The period of the anticipated noncompliance, including dates and times; and

c.
Steps being taken to prevent future occurrence of the noncompliance.


[62-620.610(17)]

18.
Sampling and monitoring data shall be collected and analyzed in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.

a.
Monitoring results shall be reported at the intervals specified elsewhere in this permit and shall be reported on a Discharge Monitoring Report (DMR), DEP Form 62-620.910(10), or as specified elsewhere in the permit.

b.
If the permittee monitors any contaminant more frequently than required by the permit, using Department approved test procedures, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the DMR.

c.
Calculations for all limitations which require averaging of measurements shall use an arithmetic mean unless otherwise specified in this permit.

d.
Except as specifically provided in Rule 62-160.300, F.A.C., any laboratory test required by this permit shall be performed by a laboratory that has been certified by the Department of Health Environmental Laboratory Certification Program (DOH ELCP).  Such certification shall be for the matrix, test method and analyte(s) being measured to comply with this permit.  For domestic wastewater facilities, testing for parameters listed in Rule 62-160.300(4), F.A.C., shall be conducted under the direction of a certified operator.

e.
Field activities including on-site tests and sample collection shall follow the applicable standard operating procedures described in DEP-SOP-001/01 adopted by reference in Chapter 62-160, F.A.C.  

f.
Alternate field procedures and laboratory methods may be used where they have been approved in accordance with Rules 62-160.220 and 62-160.330, F.A.C.

[62-620.610(18)]
19.
Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule detailed elsewhere in this permit shall be submitted no later than 14 days following each schedule date.  [62-620.610(19)]

20.
The permittee shall report to the Department any noncompliance which may endanger health or the environment.  Any information shall be provided orally within 24 hours from the time the permittee becomes aware of the circumstances.  A written submission shall also be provided within five days of the time the permittee becomes aware of the circumstances.  The written submission shall contain:  a description of the noncompliance and its cause; the period of noncompliance including exact dates and time, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.

a.
The following shall be included as information, which must be reported within 24 hours under this condition:

1.
Any unanticipated bypass which causes any reclaimed water or effluent to exceed any permit limitation or results in an intermitted discharge,

2.
Any upset which causes any reclaimed water or the effluent to exceed any limitation in the permit,

3.
Violation of a maximum daily discharge limitation for any of the pollutants specifically listed in the permit for such notice, and

4.
Any unauthorized discharge to surface or ground waters.

b.
Oral reports as required by this subsection shall be provided as follows:

1.
For unauthorized releases or spills of treated or untreated wastewater reported pursuant to subparagraph a.4 that are in excess of 1,000 gallons per incident, or where information indicates that public health or the environment will be endangered, oral reports shall be provided to the Department by calling the STATE WARNING POINT TOLL FREE NUMBER (800) 320-0519, as soon as practical, but no later than 24 hours from the time the permittee becomes aware of the discharge. The permittee, to the extent known, shall provide the following information to the State Warning Point:

a) Name, address, and telephone number of person reporting;

b) Name, address, and telephone number of permittee or responsible person for the discharge; 

c) Date and time of the discharge and status of discharge (ongoing or ceased); 

d) Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater);

e) Estimated amount of the discharge;

f) Location or address of the discharge; 

g) Source and cause of the discharge; 

h) Whether the discharge was contained on-site, and cleanup actions taken to date; 

i) Description of area affected by the discharge, including name of water body affected, if any; and  

j) Other persons or agencies contacted.

2.
Oral reports, not otherwise required to be provided pursuant to subparagraph b.1 above,  shall be provided to the Department within 24 hours from the time the permittee becomes aware of the circumstances. 

c.
If the oral report has been received within 24 hours, the noncompliance has been corrected, and the noncompliance did not endanger health or the environment, the Department shall waive the written report.


[62-620.610(20)]

21.
The permittee shall report all instances of noncompliance not reported under Permit Conditions IX. 17., 18. and 19. of this permit at the time monitoring reports are submitted.  This report shall contain the same information required by Permit Condition IX. 20 of this permit.  [62-620.610(21)]

22.
Bypass Provisions.

a.
Bypass is prohibited, and the Department may take enforcement action against a permittee for bypass, unless the permittee affirmatively demonstrates that:

1.
Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage; and 

2.
There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

3.
The permittee submitted notices as required under Permit Condition IX. 22. b. of this permit.

b.
If the permittee knows in advance of the need for a bypass, it shall submit prior notice to the Department, if possible at least 10 days before the date of the bypass.  The permittee shall submit notice of an unanticipated bypass within 24 hours of learning about the bypass as required in Permit Condition IX. 20. of this permit.  A notice shall include a description of the bypass and its cause; the period of the bypass, including exact dates and times; if the bypass has not been corrected, the anticipated time it is expected to continue; and the steps taken or planned to reduce, eliminate, and prevent  recurrence of the bypass.

c.
The Department shall approve an anticipated bypass, after considering its adverse effect, if the permittee demonstrates that it will meet the three conditions listed in Permit Condition IX. 22. a. 1. through 3. of this permit.

d.
A permittee may allow any bypass to occur which does not cause reclaimed water or effluent limitations to be exceeded if it is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of Permit Condition IX. 22. a. through c. of this permit.


[62-620.610(22)]

23.
Upset Provisions

a.
A permittee who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed contemporaneous operating logs, or other relevant evidence that:

1.
An upset occurred and that the permittee can identify the cause(s) of the upset;

2.
The permitted facility was at the time being properly operated;

3.
The permittee submitted notice of the upset as required in Permit Condition IX. 20. of this permit; and

4.
The permittee complied with any remedial measures required under Permit Condition IX. 5. of this permit.

b.
In any enforcement proceeding, the burden of proof for establishing the occurrence of an upset rests with the permittee.

c.
Before an enforcement proceeding is instituted, no representation made during the Department review of a claim that noncompliance was caused by an upset is final agency action subject to judicial review.

[62-620.610(23)]
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