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FACILITY:

	BCUD/South Beaches WWTF
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	Melbourne Beach, FL  32951

	Brevard County


Latitude: 28° 02’ 30” N      Longitude: 80° 32’ 52” W
This permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and applicable rules of the Florida Administrative Code (F.A.C.) and constitutes authorization to discharge to waters of the state under the National Pollutant Discharge Elimination System.  The above named permittee is hereby authorized to operate the facilities shown on the application and other documents attached hereto or on file with the Department and made a part hereof and specifically described as follows:

TREATMENT FACILITIES:

An existing 8.0 mgd annual average daily flow (AADF) activated sludge domestic wastewater treatment facility consisting of two (2) contiguous wastewater treatment plants (a 6.0 mgd dual train carrousel oxidation ditch and a 2.0 MGD activated sludge plant), connected in parallel with mechanical influent screening, grit removal, aeration, clarification, chemical feed facilities, disinfection by chlorination, tertiary filtration, dechlorination,  and dewatering of residuals.  

DISPOSAL:

Surface Water Discharge:  An existing 8.0 MGD permitted discharge to Indian River Lagoon (Class III marine waters) at Discharge Location (D-001) for a period not to exceed five (5) days during the Mechanical Integrity Testing of the facility’s underground injection well, in accordance with Conditions I.A.8. through I.A.11. of this permit.  The permitted discharge of 8.0 MGD over five (5) days will equate to a 0.11 MGD AADF.  The point of discharge is located approximately at latitude 28 o 02' 30" N, longitude 80 o 32' 50" W.  The discharge is located in the Waterbody Identification (WBID) number 2963A.  
Underground Injection:   An existing 8.0 MGD AADF permitted capacity underground injection well system U-001 consisting of one (1) Class I underground injection well permitted under Department permit number(s) 05-0185898-001 discharging to Class G-IV ground water.  Underground injection well system U-001 is located approximately at latitude 28 o 2' 30" N, longitude 80 o 32' 52" W. 

REUSE:

Land Application:  An existing slow-rate public access land application system (R-001) consisting of a reclaimed water transmission/distribution system for public access irrigation of residential lawns, golf courses, parks, playgrounds and landscaped areas within the Reuse Service Area, as shown on the attached map.  The existing reuse capacity is 1.422 mgd AADF, with a total anticipated reuse capacity of 3.0 mgd AADF, as listed in Condition IV. 1 of this permit. System R-001 includes the Spessard Holland Golf Course where reclaimed water is stored in an existing stormwater retention pond system with a combined storage capacity of 4.31 million gallons. The pond system has an intermittent discharge from Pond #6 to adjacent drainage features, which ultimately discharges to the Indian River Lagoon. Discharge of reclaimed water to this stormwater retention pond system shall be in accordance with Condition IV.16. of this permit.
IN ACCORDANCE WITH: The limitations, monitoring requirements and other conditions set forth in Pages 1 through 25 of this permit.

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.
Surface Water Discharges

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to discharge effluent from Outfall D-001 to Indian River Lagoon (Class III Marine Water). Such discharge shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.D.11:

	 
	
	
	Effluent Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow
	MGD
	Maximum
	8.0
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-3
	See Cond. I.A.4.

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	-
	-
	-
	20.0
	Daily During Discharge
	24-hour flow proportioned composite
	EFD-1
	

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	-
	-
	20.0
	Daily During Discharge
	24-hour flow proportioned composite
	EFD-1
	

	pH
	SU
	Range
	-
	-
	-
	6.5 to 8.5
	Continuous
	Meter
	EFA-2
	See Cond. I.A.3.

	Coliform, Fecal
	#/100 ML
	Maximum
	See Permit Condition I.A.5.
	5 Days/Week
	Grab
	EFA-2
	

	Total Residual Chlorine (For Disinfection)
	MG/L
	Minimum
	-
	-
	-
	1.0
	Continuous
	Meter
	EFA-2
	See Cond. I.A.3., 6.

	Total Residual Chlorine (For Dechlorination)
	MG/L
	Maximum
	-
	-
	-
	0.01
	Daily During Discharge
	Grab
	EFD-1
	

	Nitrogen, Total (as N)
	MG/L
	Maximum
	-
	-
	-
	12.0
	Daily During Discharge
	24-hour flow proportioned composite
	EFD-1
	

	Phosphorus, Total  (as P)
	MG/L
	Maximum
	-
	-
	-
	4.0
	Daily During Discharge
	24-hour flow proportioned composite
	EFD-1
	

	Oxygen, Dissolved  (DO)
	MG/L
	Minimum
	-
	-
	-
	5.0
	Daily During Discharge
	Grab
	EFD-1
	

	Whole Effluent Toxicity
	See Permit Condition I.A.7
	One time During Discharge
	Grab
	EFD-1
	


Surface Water Discharges (D001, Cont.)
	
	
	
	Effluent Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/
Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Phosphorus, Total  (as P)
	LB/YR
	Maximum
	*36.0
	-
	-
	-
	Monthly
	Calculated
	EFD-1
	See Note 1

	Nitrogen, Total
	LB/YR
	Maximum
	*173.0
	-
	-
	-
	Monthly
	Calculated
	EFD-1
	See Note 1


Note 1:  The annual average mass loadings given are based on the final EPA TMDL from Outfall D001 to the Indian River Lagoon, and are based on the calendar year (January through December).

Note 2:  In addition to the specified limits, the monthly average effluent CBOD5 and total suspended solids concentrations shall not exceed 10% of the respective influent values (85% Removal)

2. Effluent samples shall be taken at the monitoring site locations listed in Permit Condition I. A.  1. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-2
	Sampling point at chlorine contact chamber/effluent equalization basin

	EFD-1
	Sampling point after dechlorination and prior to the holding pond

	FLW-3
	Flow meter for discharge to river during mechanical integrity testing


3. Hourly measurement of pH and total residual chlorine for disinfection during the period of required operator attendance may be substituted for continuous measurement. [Chapter 62-601, Figure 2]
4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually. [62-601.200(17) and .500(6)]
5. The arithmetic mean of the monthly fecal coliform values collected during an annual period shall not exceed 14 per 100 mL of effluent sample.  The median value of the fecal coliform values for a minimum number of 10 samples of effluent each collected on a separate day during a period of 30 consecutive days (monthly), shall not exceed 14 per 100 mL of sample.  No more than 10 percent of the samples collected (the 90th percentile value) during a period of 30 consecutive days shall exceed 43 fecal coliform values per 100 mL of sample.  Any one sample shall not exceed 86 fecal coliform values per 100 mL of sample. Note: To report the 90th percentile value, list the fecal coliform values obtained during the month in ascending order. Report the value of the sample that corresponds to the 90th percentile (multiply the number of samples by 0.9).  For example, for 30 samples, report the corresponding fecal coliform number for the 27th value of ascending order. [62-600.440(6)(c)] 
6. A minimum of 1.0 mg/L total residual chlorine must be maintained for a minimum contact time of 15 minutes based on peak hourly flow. [62-600.440(5)(b) and (6)(b)]
7. The permittee shall comply with the following requirements to evaluate acute whole effluent toxicity of the discharge from outfall D-001. 

a. Effluent Limitation 

(1) Whole effluent acute toxicity shall not exceed in any routine or in any additional follow-up test an LC50 of less than 100% effluent. [Rules 62-302.200(1), 62-302.500(1)(a)4., 62-4.244(3)(a), and 62-4.241(1)(a) or 2(a), F.A.C.] 

b. Monitoring Frequency 

(1) Routine toxicity tests shall be conducted once when there is a discharge from D-001. The test shall be collected the first time there is a discharge during the permit cycle. 

c. Sampling Requirements 

(1) Routine tests shall be conducted on four separate grab samples collected at evenly-spaced (6-hr) intervals over a 24-hour period. The four grab samples shall be used in eight bioassays (four bioassays for each species) and shall represent one test. If the duration of the discharge is less than 24-hours, the duration of discharge shall be documented on the chain of custody. 

(2) For additional follow-up tests, the first test shall be conducted on four separate grab samples collected at evenly-spaced (6-hr) intervals over a 24-hour period. The four grab samples shall be used in four separate bioassays for each species that failed the routine test. The four grab samples represent one test. The second follow-up test shall be run on a single grab sample collected on the day and time when the greatest toxicity was identified in the routine or first additional follow-up test. Results for each additional test shall include the determination of LC50 values with 95% confidence limits. 

d. Test Requirements 

(1) Routine Tests: All routine tests shall be conducted using a control (0% effluent) and a minimum of five dilutions: 100%, 75%, 50%, 25%, and 12.5% effluent. 

(2) The permittee shall conduct 96-hour acute static renewal multi-concentration toxicity tests using the daphnid, Ceriodaphnia dubia, and the bannerfin shiner, Cyprinella leedsi, concurrently. 

(3) All test species, procedures and quality assurance criteria used shall be in accordance with Methods for Measuring Acute Toxicity of Effluents and Receiving Waters to Freshwater and Marine Organisms, EPA-821-R-02-012. Any deviation of the bioassay procedures outlined herein shall be submitted in writing to the Department for review and approval prior to use. In the event the above method is revised, the permittee shall conduct acute toxicity testing in accordance with the revised method. 

(4) The control water and dilution water shall be moderately hard water as described in EPA-821-R-02-012, Table 7. 

e. Quality Assurance Requirements 

(1) A standard reference toxicant (SRT) quality assurance (QA) acute toxicity test shall be conducted with each species used in the required toxicity tests either concurrently or initiated no more than 30 days before the date of each routine or additional follow-up test conducted. Additionally, the SRT test must be conducted concurrently if the test organisms are obtained from outside the test laboratory unless the test organism supplier provides control chart data from at least the last five monthly acute toxicity tests using the same reference toxicant and test conditions. If the organism supplier provides the required SRT data, the organism supplier’s SRT data and the test laboratory’s monthly SRT-QA data shall be included in the reports for each companion routine or additional follow-up test required. 

(2) If the mortality in the control (0% effluent) exceeds 10% for either species in any test, the test for that species (including the control) shall be invalidated and the test repeated. The repeat test shall begin within 14 days after the last day of the invalid test. 

(3) If 100% mortality occurs in all effluent concentrations prior to the end of any test and the control mortality is less than 10% at that time, the test (including the control) shall be terminated with the conclusion that the test fails and constitutes non-compliance. 

(4) Additional follow-up tests shall be evaluated for acceptability based on the concentration-response relationship, as required by EPA-821-R-02-012, Section 12.2.6.2., and included with the bioassay laboratory reports. 

f. Reporting Requirements 

(1) Results from all required tests shall be reported on the Discharge Monitoring Report (DMR) as follows: 

(a) Routine Test Results: If an LC50 >100% effluent occurs in all four separate grab sample tests for the test species, “>100%” shall be entered on the DMR for that test species. If in any of the four separate grab sample tests for the test species an LC50 <100% effluent occurs, the lowest calculated LC50 effluent concentration shall be entered on the DMR for that test species. 

(b) Additional Follow-up Test Results: For each additional test required, the calculated LC50 value shall be entered on the DMR for that test species and the 95% confidence limits. 

(2) A bioassay laboratory report for the routine test shall be prepared according to EPA-821-R-02-012, Section 12, Report Preparation and Test Review, and mailed to the Department at the address below within 30 days after the last day of the test. 

(3) For additional follow-up tests, a single bioassay laboratory report shall be prepared according to EPA-821-R-02-012, Section 12, and mailed within 30 days after the last day of the second valid additional follow-up test. 

(4) Data for invalid tests shall be included in the bioassay laboratory report for the repeat test. 

(5) The same bioassay data shall not be reported as the results of more than one test. 

(6) All bioassay laboratory reports shall be sent to: 

Florida Department of Environmental Protection 

Central District 

3319 Maguire Boulevard Suite 232 

Orlando, Florida 32803-3767 

g. Test Failures 

(1) A test fails when the test results do not meet the limits in 7.a.(1). 

(2) Additional Follow-up Tests: 

(a) If a routine test does not meet the acute toxicity limitation in 7.a.(1) above, the permittee shall notify the Department at the address above within 21 days after the last day of the failed routine test and conduct two additional follow-up tests on each species that failed the test in accordance with 7.d. 

(b) The first test shall be initiated upon the next discharge event from D-001. The remaining additional follow-up tests shall be conducted weekly thereafter or at the following discharge event until a total of two valid additional follow-up tests are completed. 

(c) The first additional follow-up test shall be conducted using a control (0% effluent) and a minimum of five dilutions: 100%, 75%, 50%, 25%, and 12.5% effluent. The permittee may modify the dilution series in the second additional follow-up test to more accurately bracket the toxicity such that at least two dilutions above and two dilutions below the target concentration and a control (0% effluent) are run. All test results shall be statistically analyzed according to the Appendices in EPA-821-R-02-012. 

(3) In the event of three valid test failures (whether routine or additional follow-up tests) within a 12-month period, the permittee shall notify the Department within 21 days after the last day of the third test failure. 

(a) The permittee shall submit a plan for correction of the effluent toxicity within 60 days after the last day of the third test failure. 

(b) The Department shall review and approve the plan before initiation. 

(c) The plan shall be initiated within 30 days following the Department’s written approval of the plan. 

(d) Progress reports shall be submitted quarterly to the Department at the address above. 

(e) During the implementation of the plan, the permittee shall conduct quarterly routine whole effluent toxicity tests in accordance with 7.d. Additional follow-up tests are not required while the plan is in progress. Following completion or termination of the plan, the frequency of monitoring for routine and additional follow-up tests shall return to the schedule established in 7.b.(1). If a routine test is invalid according to the acceptance criteria in EPA-821-R-02-012, a repeat test shall be initiated within 14 days after the last day of the invalid routine test. 

(f) Upon completion of four consecutive, valid routine tests that demonstrate compliance with the effluent limitation in 7.a.(1) above, the permittee may submit a written request to the Department to terminate the plan. The plan shall be terminated upon written verification by the Department that the facility has passed at least four consecutive valid routine whole effluent toxicity tests. If a test within the sequence of the four is deemed invalid, but is replaced by a repeat valid test initiated within 14 days after the last day of the invalid test, the invalid test will not be counted against the requirement for four consecutive valid tests for the purpose of terminating the plan. 

(4) The additional follow-up testing and the plan do not preclude the Department taking enforcement action for whole effluent toxicity permit limit violations. 

[62-4.241, 62-620.620(3)]
8. During the next surface water discharge event effluent testing shall be conducted in accordance with the instructions for Section 3A, item 14 of permit application Form 2A at Monitoring Location Site Number EFD-1.  The results shall be submitted on the tables in Form 2A to the Department’s Central District Office.  The results of these analyses shall be evaluated to determine if there is reasonable assurance that the effluent will comply with water quality standards.  Based on the results, the Department shall reserve the right to revise this permit to incorporate additional monitoring or effluent limits for the surface water discharge. [62-620.910(2)]

9. The permittee shall submit written notification to the Department, thirty (30) days prior to a scheduled underground injection well mechanical integrity test (MIT).  Such notification must include the proposed date(s) for the test and indicate whether or not a discharge is expected due to the test.  The performance of the MIT shall be contingent upon passing the toxicity tests required in Condition I.A.7. of this permit. [62-4-070(3)]
10. The surface water discharge can be continued after mechanical integrity testing has been performed, if the Department concurs in the prohibition of further injection well use due to technical problems identified during the test.  If the discharge is continued beyond the period required for mechanical integrity testing, this permit may be modified to include more stringent effluent limitations as necessary to protect the water quality of the receiving water body and/or to include a compliance schedule for eliminating the surface water discharge. [62-4-070(3)]
11. The Total Maximum Daily Load (TMDL) for the Indian River Lagoon was finalized by EPA in April 2007.  The TMDL includes a wasteload allocation of:

173 lb/year for Total Nitrogen 

36 lb/year for Total Phosphorus 

The Department is developing a Total Maximum Daily Load (TMDL) for the Indian River Lagoon during the life of this permit that would replace the EPA TMDL, once approved.  If an alternate TMDL for this water body is established and adopted by rule, the Department may revise this permit to incorporate the final TMDL, pursuant to Rule 62-620.325, Florida Administrative Code.

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS (cont.)

B.
Underground Injection Control Systems

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to discharge effluent to Underground Injection Well Facility U-001 located at latitude 28 o 2' 30" N, longitude 80 o 32' 52" W.  Such discharge shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.D.11:

	 
	
	
	Effluent Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow
	MGD
	Maximum
	8.0
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-1
	See Cond. I.B.3.

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	5 Days/Week
	24-hour flow proportioned composite
	EFA-2
	

	Solids, Total  Suspended
	MG/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	5 Days/Week
	24-hour flow proportioned composite
	EFA-2
	

	pH
	SU
	Range
	-
	-
	-
	6.0 to 8.5
	Daily
	Grab
	EFA-2
	


2. Effluent samples shall be taken at the monitoring site locations listed in Permit Condition I. B.  1. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-2
	Sampling point at chlorine contact chamber/ effluent equalization basin

	FLW-1
	Flow meter for the injection well


3. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually. [62-601.200(17) and .500(6)]  

4. Disinfection is not required for discharge to Class G‑IV waters using Class I wells.  However, the permittee must maintain the capability for disinfection at a level that is consistent with the alternate disposal mechanism approved for this facility pursuant to Rule 62‑600.540(5), F.A.C. [62-600.540(1)]  

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS (cont.)

C.
Reuse and Land Application Systems

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to direct reclaimed water to Reuse System R-001.  Such reclaimed water shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.D.11:

	 
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow
	MGD
	Maximum
	3.0
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-2
	See Cond. I.C.4.

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	5 Days/Week
	24-hour flow proportioned composite
	EFA-1
	

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	-
	-
	5.0
	4 Days/Week
	Grab
	EFB-1
	

	pH
	SU
	Range
	-
	-
	-
	6.0 to 8.5
	Continuous
	Meter
	EFA-1
	See Cond. I.C.3.

	Coliform, Fecal, % less than detection
	PER CENT
	Minimum
	See Permit Condition I.C.5.
	4 Days/Week
	Grab
	EFA-1
	

	Coliform, Fecal
	#/100 ML
	Maximum
	See Permit Condition I.C.5.
	4 Days/Week
	Grab
	EFA-1
	

	Total Residual Chlorine (For Disinfection)
	MG/L
	Minimum
	-
	-
	-
	1.0
	Continuous
	Meter
	EFA-1
	See Cond. I.C.6.

	Turbidity
	NTU
	Maximum
	See Permit Condition I.C.7.
	Continuous
	Meter
	EFB-1
	

	Giardia
	CYSTS/ 100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-1
	

	Cryptosporidium
	OOCYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-1
	


2. Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I. C.  1. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-1
	Sampling point at discharge of chlorine contact chamber

	EFB-1
	Sampling point after filtration and prior to disinfection

	FLW-2
	Flow meter for the reuse system and golf course irrigation


3. Hourly measurement of pH during the period of required operator attendance may be substituted for continuous measurement.  [Chapter 62-601, Figure 2]  

4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.  Note:  To report the “% less than detection,” count the number of fecal coliform observations that were less than detection, divide by the total number of fecal coliform observations in the month, and multiply by 100% (round to the nearest integer).  [62-600.440(5)(f)]  

6. The minimum total chlorine residual shall be limited as described in the approved operating protocol, such that the permit limitation for fecal coliform bacteria will be achieved.  In no case shall the total chlorine residual be less than 1.0 mg/L.  [62-600.440(5)(b); 62-610.460(2); and 62-610.463(2)]  

7. The maximum turbidity shall be limited as described in the approved operating protocol, such that the permit limitations for total suspended solids and fecal coliforms will be achieved.  [62-610.463(2)]  

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS (cont.)

D.
Other Limitations and Monitoring and Reporting Requirements

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the treatment facility shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.D.11:

	
	
	
	Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow
	MGD
	Maximum
	8.0
	-
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-4
	See Cond. I.D.4.

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	-
	Report
	-
	-
	5 Days/Week
	24-hour flow proportioned composite
	INF-1
	See Cond. I.D.3.

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	Report
	-
	-
	5 Days/Week
	24-hour flow proportioned composite
	INF-1
	See Cond. I.D.3.

	Percent Capacity, (TMADF/Permitted Capacity) x 100
	PER CENT
	Maximum
	-
	Report
	-
	-
	Monthly
	Calculated
	FLW-4
	


2. Samples shall be taken at the monitoring site locations listed in Permit Condition I. D. 1 and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	FLW-4
	Influent flow meter at headworks

	INF-1
	Automatic sampler upstream of return activated sludge (RAS) line


3. Influent samples shall be collected so that they do not contain digester supernatant or return activated sludge, or any other plant process recycled waters. [62-601.500(4)]
4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. The treatment facilities shall be operated in accordance with all approved operating protocols.  Only reclaimed water that meets the criteria established in the approved operating protocol(s) may be released to system storage or to the reuse system.  Reclaimed water that fails to meet the criteria in the approved operating protocol(s) shall be directed to the following permitted alternate discharge system: Underground injection well. The operating protocol(s) shall be reviewed and updated periodically to ensure continuous compliance with the minimum treatment and disinfection requirements.  Updated operating protocols shall be submitted to the Department for review and approval upon revision of the operating protocol(s) and with each permit application.  [62-610.320(6) and 62-610.463(2)]  

6. Instruments for continuous on-line monitoring of total residual chlorine and turbidity shall be equipped with an automated data logging or recording device.  [62-610.463(2) & .865(8)(d)]
7. Intervals between sampling for Giardia and Cryptosporidium shall not exceed two years.  Sampling results shall be reported on DEP Form 62-610.300(4)(a)4 which is attached to this permit.  This form shall be submitted to the Department and to DEP’s Reuse Coordinator in Tallahassee.  [62-610.463(4)]
8. Parameters which must be monitored as a result of a surface water discharge shall be analyzed using a sufficiently sensitive method to assure compliance with applicable water quality standards and effluent limitations in accordance with 40 CFR (Code of Federal Regulations) Part 136.  All monitoring shall be representative of the monitored activity. [62-620.320(6)]
9. The sample collection, analytical test methods and method detection limits (MDLs) applicable to this permit shall be in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.  The list of Department established analytical methods, and corresponding MDLs (method detection limits) and PQLs (practical quantitation limits), which is titled “FAC 62-4 MDL/PQL Table” is available at http://www.dep.state.fl.us/labs/guidance/index.htm.  The MDLs and PQLs as described in this list shall constitute the minimum acceptable MDL/PQL values and the Department shall not accept results for which the laboratory's MDLs or PQLs are greater than those described above unless alternate MDLs and/or PQLs have been specifically approved by the Department for this permit. Any method included in the list may be used for reporting as long as it meets the following requirements: 

a)
The laboratory’s reported MDL and PQL values for the particular method must be equal or less than the corresponding method values specified in the Department’s approved MDL and PQL list;

b)
The laboratory reported MDL for the specific parameter is less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Parameters that are listed as “report only” in the permit shall use methods that provide a MDL, which is equal to or less than the applicable water quality criteria stated in 62-302, F.A.C.; and

c)
If the MDLs for all methods available in the approved list are above the stated permit limit or applicable water quality criteria for that parameter, then the method with the lowest stated MDL shall be used.

Where necessary, the permittee may request approval of alternate methods or for alternative MDLs or PQLs for any approved analytical method.  Approval of alternate laboratory MDLs or PQLs are not necessary if the laboratory reported MDLs and PQLs are less than or equal to the permit limit or the applicable water quality criteria, if any, stated in Chapter 62-302, F.A.C.  Approval of an analytical method not included in the above-referenced list is not necessary if the analytical method is in accordance with 40 CFR 136.   [62-4.246, 62-160] 

10. The permittee shall provide safe access points for obtaining representative influent, reclaimed water, and effluent samples which are required by this permit. [62-601.500(5)]
11. Monitoring requirements under this permit are effective on the first day of the second month following permit issuance.  Until such time, the permittee shall continue to monitor and report in accordance with previously effective permit requirements, if any.  During the period of operation authorized by this permit, the permittee shall complete and submit to the Department Discharge Monitoring Reports (DMRs) in accordance with the frequencies specified by the REPORT type (i.e., monthly, toxicity, quarterly, semiannual, annual, etc.) indicated on the DMR forms attached to this permit.  Monitoring results for each monitoring period shall be submitted in accordance with the associated DMR due dates below.  

	REPORT Type
	Monitoring Period
	Due Date

	Monthly or Toxicity
	first day of month – last day of month
	28th day of following month

	Quarterly
	January 1 - March 31
April 1 – June 30
July 1 – September 30 
October 1 – December 31 
	April 28
July 28
October 28
January 28

	Semiannual
	January 1 – June 30
July 1 – December 31 
	July 28
January 28

	Annual
	January 1 – December 31
	January 28 


DMRs shall be submitted for each required monitoring period including months of no discharge.  The permittee shall make copies of the attached DMR form(s) and shall submit the completed DMR form(s) to the Department by the twenty-eighth (28th) of the month following the month of operation at the address specified below: 

Florida Department of Environmental Protection

Wastewater Compliance Evaluation Section, Mail Station 3551

Bob Martinez Center
2600 Blair Stone Road

Tallahassee, Florida 32399-2400

[62-620.610(18)][62-601.300(1),(2), and (3)]
13. During the period of operation authorized by this permit, reclaimed water or effluent shall be monitored annually for the primary and secondary drinking water standards contained in Chapter 62-550, F.A.C., (except for asbestos, color, and corrosivity).  These monitoring results shall be reported to the Department’s Central District Office annually on the DMR.  During years when a permit is not renewed, a certification stating that no new non-domestic wastewater dischargers have been added to the collection system since the last reclaimed water or effluent analysis was conducted may be submitted in lieu of the report.  The annual reclaimed water or effluent analysis report or the certification shall be completed and submitted in a timely manner so as to be received by Department’s Central District Office by June 28 of each year.  Approved analytical methods identified in Rule 62-620.100(3)(j), F.A.C., shall be used for the analysis.  If no method is included for a parameter, methods specified in Chapter 62-550, F.A.C., shall be used.  [62-601.300(4)][62-601.500(3)][62-610.300(4)]
14. The permittee shall submit an Annual Reuse Report using DEP Form 62-610.300(4)(a)2. on or before January 1 of each year.  [62-610.870(3)]
15. The permittee shall maintain an inventory of storage systems.  The inventory shall be submitted to the Department at least 30 days before reclaimed water will be introduced into any new storage system.  The inventory of storage systems shall be attached to the annual submittal of the Annual Reuse Report.  [62-610.464(5)]
16. Unless specified otherwise in this permit, all reports and other information required by this permit, including 24-hour notifications, shall be submitted to or reported to, as appropriate, the Department's Central District Office at the address specified below:

Central District Office

3319 Maguire Boulevard Suite 232
Orlando, Florida  32803-3767

Phone Number - (407) 894-7555

FAX Number -  (407) 897-2966   

All FAX copies shall be followed by original copies.  All reports and other information shall be signed in accordance with the requirements of Rule 62-620.305, F.A.C.  [62-620.305]
II.
RESIDUALS MANAGEMENT REQUIREMENTS 

1.  The method of residuals use or disposal by this facility is disposal in a Class I or II solid waste landfill.

2.  The permittee shall be responsible for proper treatment, management, use, and land application or disposal of its residuals.  [62-640.300(5)]
3. Disposal of residuals, septage, and other solids in a solid waste landfill, or disposal by placement on land for purposes other than soil conditioning or fertilization, such as at a monofill, surface impoundment, waste pile, or dedicated site, shall be in accordance with Chapter 62-701, F.A.C.  [62-640.100(6)(k)3 & 4]  

4. If the permittee intends to accept residuals from other facilities, a permit revision is required pursuant to Rule 62-640.880(2)(d), F.A.C. [62-640.880(2)(d)]  

5. Storage of residuals or other solids at the permitted facility shall require prior written notification to the Department.  [62-640.300(4)]  

III.
GROUND WATER REQUIREMENTS

Construction Requirements
Section Construction Requirements is not applicable to this facility.

Operational Requirements
1. For the Part III Public Access system, all ground water quality criteria specified in Chapter 62-520, F.A.C., shall be met at the edge of the zone of discharge.  For major users of reclaimed water (i.e., using 0.1 mgd or more), the zone of discharge shall extend horizontally 100 feet from the application site or to user’s site property line, whichever is less, and vertically to the base of the surficial aquifer.  For other users, the zone of discharge shall extend horizontally to the boundary of the general service area identified in the attached map and vertically to the base of the surficial aquifer.  [62-520.200(23)]  [62-522.400 and 62-522.410]  

2. The ground water minimum criteria specified in Rule 62-520.400 F.A.C., shall be met within the zone of discharge.  [62-520.400 and 62-520.420(4)]
3. During the period of operation authorized by this permit, the permittee shall sample ground water in accordance with this permit and the approved ground water monitoring plan prepared in accordance with Rule 62-522.600, F.A.C.  [62-522.600][62-610.463]
4. Ground water monitoring for U-001 shall be in accordance with the Underground Injection Control (UIC) permit number(s) UO05-0185898-001.

5. The following monitoring wells shall be sampled quarterly.  Sampling must be reasonably spaced to be representative of potentially changing conditions:

	Facility

MW Name
	Permit Builder

MW ID
	GMS #
	WAFR #
	Depth

(Feet)
	Aquifer Monitored
	Well Type
	New or

Existing

	At WWTF
	
	
	
	
	
	
	

	Site 1 North
	MWC-1
	3005A10102
	2064
	20
	Surficial
	Compliance
	Existing

	Site 2 East
	MWC-2
	3005A10104
	2062
	20
	Surficial
	Compliance
	Existing

	Site 3 South
	MWI-3
	3005A10103
	2063
	20
	Surficial
	Intermediate
	Existing

	Site 4 West
	MWB-4
	3005A10105
	2061
	20
	Surficial
	Background
	Existing

	Doug Flutie Park
	
	
	
	
	
	
	

	MW-1
	MWC-1 Doug Flutie
	3005A16870
	2057
	24.6
	Surficial
	Compliance
	Existing

	MW-2
	MWI-2 Doug Flutie
	3005A16871
	2056
	12.5
	Surficial
	Intermediate
	Existing

	Spessard Holland Golf Course
	
	
	
	
	
	
	

	MW-3
	MWC-3 Spessard
	3005A16872
	2055
	27.8
	Surficial
	Compliance
	Existing

	MW-4
	MWC-4 Spessard
	3005A16873
	2054
	14.3
	Surficial
	Compliance
	Existing


MWB = Background;  MWI = Intermediate;  MWC = Compliance
[62-522.600][62-610.463]  

6. The following parameters shall be analyzed for each of the monitoring well(s) identified in Permit Condition(s) III. 5:

	Parameter
	Compliance Well Limit
	Units
	Sample Type
	Monitoring Frequency

	Water Level Relative to Feet, NGVD
	Report
	FEET
	In Situ
	Quarterly

	Nitrogen, Nitrate, Total (as N)
	10
	mg/L
	Grab
	Quarterly

	Solids, Total Dissolved (TDS)
	500
	mg/L
	Grab
	Quarterly

	Chloride (as Cl)
	250
	mg/L
	Grab
	Quarterly

	Coliform, Fecal
	4
	#/100ML
	Grab
	Quarterly

	pH
	8.5
	SU
	Grab
	Quarterly

	Turbidity
	Report
	NTU
	Grab
	Quarterly

	Sodium
	160
	mg/L
	Grab
	Quarterly

	Trihalomethane, Total by summation
	80
	ug/L
	Grab
	Quarterly


[62-522.600(11)(b)] [62-601.300(3), 62-601.700, and Figure 3 of 62-601][62-601.300(6)] [62-520.300(9)]
7. If the concentration for any constituent listed in Permit Condition III. 6. in the natural background quality of the ground water is greater than the stated maximum, or in the case of pH is also less than the minimum, the representative natural background quality shall be the prevailing standard.  [62-520.420(2)]  

8. In accordance with Part D of Form 62-620.910(10), water levels shall be recorded before evacuating wells for sample collection.  Elevation references shall include the top of the well casing and land surface at each well site (Feet, NGVD) at a precision of plus or minus 0.1 foot.  [62-610.463(3)(a)]  

9. Ground water monitoring wells shall be purged prior to sampling to obtain representative samples.  [62-601.700(5)]  

10. Analyses shall be conducted on unfiltered samples, unless filtered samples have been approved by the Department's Central District, Ground Water Section as being more representative of ground water conditions.  [62-520.300(9)]  

11. Ground water monitoring parameters shall be analyzed in accordance with Chapter 62-601, F.A.C.  [62-620.610(18)]  

12. Ground water monitoring test results shall be submitted on Part D of Form 62-620.910(10). A completed Certification Page shall accompany each quarter of monitoring data. For reuse or land application projects, the quarterly ground water monitoring results shall be submitted with the DMR as shown in the following schedule. [62-4.070(3)]  [62-522.600(10) and (11)(b)]  [62-601.300(3), 62.601.700, and Figure 3 of 62-601] [62-620.610(18)]
	SAMPLE PERIOD
	REPORT DUE DATE

	January - March
	April 28

	April - June
	July 28

	July - September
	October 28

	October - December
	January 28


13. If any monitoring well becomes damaged or cannot be sampled for any reason, the permittee shall notify the Department's Central District, Ground Water Section within 24 hours of the permittee becoming aware of the situation and shall follow with a written report within seven days that details the circumstances and remedial measures taken or proposed.   Repair or replacement of monitoring wells shall be approved in advance by the Department's Central District, Ground Water Section.  [62-522.600][62-4.070(3)]
14. The Permittee shall provide verbal notice to the Department's Central District, Ground Water Section as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The Permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department's Central District, Ground Water Section in a written report within 7 days of the sinkhole discovery.  [62-4.070(3)]
IV.
ADDITIONAL REUSE AND LAND APPLICATION REQUIREMENTS

Part III Public Access System(s) (R-001)
1. This reuse system includes the following major users (i.e., using 0.1 MGD or more of reclaimed water):

	User Name
	User Type
	Capacity

(MGD)
	Acreage

	Spessard Holland Golf Course
	Golf Courses
	0.993
	80

	Doug Flutie Park
	Athletic Complexes and Parks
	0.124
	16

	Residential
	Residential developments
	0.3
	35.9

	South Beaches Plant
	Industrial and Manufacturing Facilities
	0.0047
	1.2

	Totals
	1.422
	133.1


[62-610.800(5)][62-620.630(10)(b)]
2. Cross-connections to the potable water system are prohibited.  [62-610.469(7)]
3. A cross-connection control program shall be implemented and/or remain in effect within the areas where reclaimed water will be provided for use.  [62-610.469(7)]
4. The permittee shall conduct inspections within the reclaimed water service area to verify proper connections, to minimize illegal cross-connections, and to verify the proper use of reclaimed water.  Inspections are required when a customer first connects to the reuse distribution system.  Subsequent inspections are required as specified in the cross-connection control and inspection program.  [62-610.469(7)(h)]
5. If a cross-connection between the potable and reclaimed water systems is discovered, the permittee shall:

a.
Immediately discontinue potable water and/or reclaimed water service to the affected area.

b.
If the potable water system is contaminated, clear the potable water lines.

c.
Eliminate the cross-connection.

d.
Test the affected area for other possible cross-connections.

e.
Within 24 hours, notify the Central District Office's domestic wastewater and drinking water programs.

f.
Within 5 days of discovery of a cross-connection, submit a written report to the Department detailing: a description of the cross-connection, how the cross-connection was discovered, the exact date and time of discovery, approximate time that the cross-connection existed, the location, the cause, steps taken to eliminate the cross-connection, whether reclaimed water was consumed, and reports of possible illness, whether the drinking water system was contaminated and the steps taken to clear the drinking water system, when the cross-connection was eliminated, plan of action for testing for other possible cross-connections in the area, and an evaluation of the cross-connection control and inspection program to ensure that future cross-connections do not occur.  [62-555.350(3) and 62-555.360][62-620.610(20)]
6. Maximum obtainable separation of reclaimed water lines and potable water lines shall be provided and the minimum separation distances specified in Rule 62-610.469(7), F.A.C., shall be provided.  Reuse facilities shall be color coded or marked.  Underground piping which is not manufactured of metal or concrete shall be color coded using Pantone Purple 522C using light stable colorants.  Underground metal and concrete pipe shall be color coded or marked using purple as the predominant color.  [62-610.469(7)]
7. In constructing reclaimed water distribution piping, the permittee shall maintain a 75-foot setback distance from a reclaimed water transmission facility to public water supply wells.  No setback distances are required to other potable water supply wells or to any nonpotable water supply wells.  [62-610.471(3)]
8. A setback distance of 75 feet shall be maintained between the edge of the wetted area and potable water supply wells, unless the utility adopts and enforces an ordinance prohibiting potable water supply wells within the reuse service area.  No setback distances are required to any nonpotable water supply well, to any surface water,  to any developed areas, or to any private swimming pools, hot tubs, spas, saunas, picnic tables, barbecue pits, or barbecue grills.  [62-610.471(1), (2), (5), and (7)]
9. Reclaimed water shall not be used to fill swimming pools, hot tubs, or wading pools.  [62-610.469(4)]
10. Low trajectory nozzles, or other means to minimize aerosol formation shall be used within 100 feet from outdoor public eating, drinking, or bathing facilities.  [62-610.471(6)]
11. A setback distance of 100 feet shall be maintained from indoor aesthetic features using reclaimed water to adjacent indoor public eating and drinking facilities.  [62-610.471(8)]
12. The public shall be notified of the use of reclaimed water.  This shall be accomplished by posting of advisory signs in areas where reuse is practiced, notes on scorecards, or other methods.  [62-610.468(2)]
13. All new advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets shall bear the words “do not drink” and “no beber” along with the equivalent standard international symbol.  In addition to the words “do not drink” and “no beber,” advisory signs posted at storage ponds and decorative water features shall also bear the words “do not swim” and “no nadar” along with the equivalent standard international symbols.  Existing advisory signs and labels shall be retrofitted, modified, or replaced in order to comply with the revised wording requirements.  For existing advisory signs and labels this retrofit, modification, or replacement shall occur within 365 days after the date of this permit.  For labels on existing vaults, service boxes, or compartments housing hose bibbs this retrofit, modification, or replacement shall occur within 730 days after the date of this permit.  [62-610.468 & 62-610.469]
14. The permittee shall ensure that users of reclaimed water are informed about the origin, nature, and characteristics of reclaimed water; the manner in which reclaimed water can be safely used; and limitations on the use of reclaimed water. Notification is required at the time of initial connection to the reclaimed water distribution system and annually after the reuse system is placed into operation.  A description of on-going public notification activities shall be included in the Annual Reuse Report.  [62-610.468(6)]
15. Routine aquatic weed control and regular maintenance of storage pond embankments and access areas are required.  [62-610.414 & 62-610.464]
16. Overflows from emergency discharge facilities on storage ponds shall be reported as an abnormal event to the Department's Central District Office within 24 hours of an occurrence.  The provisions of Rule 62-610.800(9), F.A.C., shall be met.  [62-610.800(9)]
V.
OPERATION AND MAINTENANCE REQUIREMENTS

1.
During the period of operation authorized by this permit, the wastewater facilities shall be operated under the supervision of a(n) operator(s) certified in accordance with Chapter 62-602, F.A.C.  In accordance with Chapter 62-699, F.A.C., this facility is a Category I, Class A facility and, at a minimum, operators with appropriate certification must be on the site as follows:

A Class C or higher operator 24 hours/day for 7 days/week.  The lead operator must be a Class A.

[62-620.630(3)] [62-699.310] [62-610.462]
2. The lead operator shall be employed at the plant full time.  “Full time” shall mean at least 4 days per week, working a minimum of 35 hours per week, including leave time.  A certified operator shall be on-site and in charge of each required shift and for periods of required staffing time when the lead operator is not on-site.  An operator meeting the lead operator classification level of the plant shall be available during all periods of plant operation.  “Available” means able to be contacted as needed to initiate the appropriate action in a timely manner.  [62-699.311(10), (5) and (1)]
3. The application to renew this permit shall include an updated capacity analysis report prepared in accordance with Rule 62-600.405, F.A.C.  [62-600.405(5)]
4. The application to renew this permit shall include a detailed operation and maintenance performance report prepared in accordance with Rule 62-600.735, F.A.C.  [62-600.735(1)]
5. The permittee shall maintain the following records and make them available for inspection  on the site of the permitted facility:

a.
Records of all compliance monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation and a copy of the laboratory certification showing the certification number of the laboratory, for at least three years from the date the sample or measurement was taken;

b.
Copies of all reports required by the permit for at least three years from the date the report was prepared;

c.
Records of all data, including reports and documents, used to complete the application for the permit for at least three years from the date the application was filed;

d.
Monitoring information, including a copy of the laboratory certification showing the laboratory certification number, related to the residuals use and disposal activities for the time period set forth in Chapter 62-640, F.A.C., for at least three years from the date of sampling or measurement;

e.
A copy of the current permit;

f.
A copy of the current operation and maintenance manual as required by Chapter 62-600,. F.A.C.;

g.
A copy of the facility record drawings;

h.
Copies of the licenses of the current certified operators; and 

i.
Copies of  the logs and schedules showing plant operations and equipment maintenance for three years from the date of the logs or schedules.  The logs shall, at a minimum, include identification of the plant; the signature and certification number of the operator(s) and the signature of the person(s) making any entries; date and time in and out; specific operation and maintenance activities; tests performed and samples taken; and major repairs made. The logs shall be maintained on-site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed.


[62-620.350]
VI.
SCHEDULES

1. The following improvement actions shall be completed according to the following schedule:

	Improvement Action
	Completion Date

	1
	Repair #2 RAS pump at the 6.0 MGD plant
	April 1, 2009

	2
	Repair clarifier drive at 2.0 MGD plant
	April 1, 2009


[62-600.735(1)]
VII.  INDUSTRIAL PRETREATMENT PROGRAM REQUIREMENTS

This facility is not required to have a pretreatment program at this time.  [62-625.500]
VIII.  OTHER SPECIFIC CONDITIONS

1. The permittee shall apply for renewal of this permit at least 180 days before the expiration date of the permit using the appropriate forms listed in Rule 62-620.910, F.A.C., including submittal of the appropriate processing fee set forth in Rule 62-4.050, F.A.C.  The existing permit shall not expire until the Department has taken final action on the application renewal in accordance with the provisions of 62-620.335(3) and (4), F.A.C.  [62-620.335(1)-(4)]
2. Florida water quality criteria and standards shall not be violated as a result of any discharge or land application of reclaimed water or residuals from this facility.  [62-620.320(9) and 62-302.500(2)(e)][62-610.850(1)(a) and (2)(a)]
3. In the event that the treatment facilities or equipment no longer function as intended, are no longer safe in terms of public health and safety, or odor, noise, aerosol drift, or lighting adversely affects neighboring developed areas at the levels prohibited by Rule 62-600.400(2)(a), F.A.C., corrective action (which may include additional maintenance or modifications of the permitted facilities) shall be taken by the permittee.  Other corrective action may be required to ensure compliance with rules of the Department.  Additionally, the treatment, management, use or land application of residuals shall not cause a violation of the odor prohibition in Rule 62-296.320(2), F.A.C.  [62-600.410(8) and 62-640.400(6)]
4. The deliberate introduction of stormwater in any amount into collection/transmission systems designed solely for the introduction (and conveyance) of domestic/industrial wastewater; or the deliberate introduction of stormwater into collection/transmission systems designed for the introduction or conveyance of combinations of storm and domestic/industrial wastewater in amounts which may reduce the efficiency of pollutant removal by the treatment plant is prohibited, except as provided by Rule 62-610.472, F.A.C.  [62-604.130(3)]
5. Collection/transmission system overflows shall be reported to the Department in accordance with Permit Condition IX. 20.  [62-604.550]  [62-620.610(20)]
6. The operating authority of a collection/transmission system and the permittee of a treatment plant are prohibited from accepting connections of wastewater discharges which have not received necessary pretreatment or which contain materials or pollutants (other than normal domestic wastewater constituents):

a.
Which may cause fire or explosion hazards; or

b.
Which may cause excessive corrosion or other deterioration of wastewater facilities due to chemical action or pH levels; or

c.
Which are solid or viscous and obstruct flow or otherwise interfere with wastewater facility operations or treatment; or

d.
Which result in the wastewater temperature at the introduction of the treatment plant exceeding 40oC or otherwise inhibiting treatment; or

e.
Which result in the presence of toxic gases, vapors, or fumes that may cause worker health or safety problems.

[62-604.130(5)]
7. The treatment facility, storage ponds, rapid infiltration basins, and/or infiltration trenches shall be enclosed with a fence or otherwise provided with features to discourage the entry of animals and unauthorized persons.  [62-600.400(2)(b)] 
8. Screenings and grit removed from the wastewater facilities shall be collected in suitable containers and hauled to a Department approved Class I landfill or to a landfill approved by the Department for receipt/disposal of screenings and grit.  [62-701.300(1)(a)]
9. The Permittee shall provide verbal notice to the Department as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The Permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department in a written report within 7 days of the sinkhole discovery.  [62-4.070(3)]
10. The permittee shall provide adequate notice to the Department of the following:

a.
Any new introduction of pollutants into the facility from an industrial discharger which would be subject to Chapter 403, F.S., and the requirements of Chapter 62-620, F.A.C. if it were directly discharging those pollutants; and

b.
Any substantial change in the volume or character of pollutants being introduced into that facility by a source which was identified in the permit application and known to be discharging at the time the permit was issued.


Adequate notice shall include information on the quality and quantity of effluent introduced into the facility and any anticipated impact of the change on the quantity or quality of effluent or reclaimed water to be discharged from the facility.

[62-620.625(2)]
IX.
GENERAL CONDITIONS

1.
The terms, conditions, requirements, limitations and restrictions set forth in this permit are binding and enforceable pursuant to Chapter 403, Florida Statutes.  Any permit noncompliance constitutes a violation of Chapter 403, Florida Statutes, and is grounds for enforcement action, permit termination, permit revocation and reissuance, or permit revision.  [62-620.610(1)]

2.
This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviations from the approved drawings, exhibits, specifications or conditions of this permit constitutes grounds for revocation and enforcement action by the Department.  [62-620.610(2)]
3.
As provided in subsection 403.087(7), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor authorize any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit or authorization that may be required for other aspects of the total project which are not addressed in this permit.  [62-620.610(3)]
4.
This permit conveys no title to land or water, does not constitute state recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [62-620.610(4)]

5.
This permit does not relieve the permittee from liability and penalties for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source; nor does it allow the permittee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department.  The permittee shall take all reasonable steps to minimize or prevent any discharge, reuse of reclaimed water, or residuals use or disposal in violation of this permit which has a reasonable likelihood of adversely affecting human health or the environment.  It shall not be a defense for a permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this permit.  [62-620.610(5)]
6.
If the permittee wishes to continue an activity regulated by this permit after its expiration date, the permittee shall apply for and obtain a new permit.  [62-620.610(6)]
7.
The permittee shall at all times properly operate and maintain the facility and systems of treatment and control, and related appurtenances, that are installed and used by the permittee to achieve compliance with the conditions of this permit.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to maintain or achieve compliance with the conditions of the permit.  [62-620.610(7)]

8.
This permit may be modified, revoked and reissued, or terminated for cause.  The filing of a request by the permittee for a permit revision, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition.  [62-620.610(8)]

9.
The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, including an authorized representative of the Department and authorized EPA personnel, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated, to:

a.
Enter upon the permittee’s premises where a regulated facility, system, or activity is located or conducted, or where records shall be kept under the conditions of this permit;

b.
Have access to and copy any records that shall be kept under the conditions of this permit;

c.
Inspect the facilities, equipment, practices, or operations regulated or required under this permit; and

d.
Sample or monitor any substances or parameters at any location necessary to assure compliance with this permit or Department rules.


[62-620.610(9)]

10.
In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data, and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except as such use is proscribed by Section 403.111, Florida Statutes, or Rule 62-620.302, Florida Administrative Code.  Such evidence shall only be used to the extent that it is consistent with the Florida Rules of Civil Procedure and applicable evidentiary rules.  [62-620.610(10)]

11.
When requested by the Department, the permittee shall within a reasonable time provide any information required by law which is needed to determine whether there is cause for revising, revoking and reissuing, or terminating this permit, or to determine compliance with the permit.  The permittee shall also provide to the Department upon request copies of records required by this permit to be kept.  If the permittee becomes aware of relevant facts that were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be promptly submitted or corrections promptly reported to the Department.  [62-620.610(11)]

12.
Unless specifically stated otherwise in Department rules, the permittee, in accepting this permit, agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.  A reasonable time for compliance with a new or amended surface water quality standard, other than those standards addressed in Rule 62-302.500, F.A.C., shall include a reasonable time to obtain or be denied a mixing zone for the new or amended standard.  [62-620.610(12)]

13.
The permittee, in accepting this permit, agrees to pay the applicable regulatory program and surveillance fee in accordance with Rule 62-4.052, F.A.C.  [62-620.610(13)]

14.
This permit is transferable only upon Department approval in accordance with Rule 62-620.340, F.A.C.  The permittee shall be liable for any noncompliance of the permitted activity until the transfer is approved by the Department.  [62-620.610(14)]

15.
The permittee shall give the Department written notice at least 60 days before inactivation or abandonment of a wastewater facility and shall specify what steps will be taken to safeguard public health and safety during and following inactivation or abandonment.  [62-620.610(15)]

16.
The permittee shall apply for a revision to the Department permit in accordance with Rules 62-620.300 and the Department of Environmental Protection Guide to Wastewater Permitting at least 90 days before construction of any planned substantial modifications to the permitted facility is to commence or with Rule 62-620.325(2) for minor modifications to the permitted facility.  A revised permit shall be obtained before construction begins except as provided in Rule 62-620.300, F.A.C.  [62-620.610(16)]
17.
The permittee shall give advance notice to the Department of any planned changes in the permitted facility or activity which may result in noncompliance with permit requirements.  The permittee shall be responsible for any and all damages which may result from the changes and may be subject to enforcement action by the Department for penalties or revocation of this permit.  The notice shall include the following information:

a.
A description of the anticipated noncompliance;

b.
The period of the anticipated noncompliance, including dates and times; and

c.
Steps being taken to prevent future occurrence of the noncompliance.


[62-620.610(17)]

18.
Sampling and monitoring data shall be collected and analyzed in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.

a.
Monitoring results shall be reported at the intervals specified elsewhere in this permit and shall be reported on a Discharge Monitoring Report (DMR), DEP Form 62-620.910(10), or as specified elsewhere in the permit.

b.
If the permittee monitors any contaminant more frequently than required by the permit, using Department approved test procedures, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the DMR.

c.
Calculations for all limitations which require averaging of measurements shall use an arithmetic mean unless otherwise specified in this permit.

d.
Except as specifically provided in Rule 62-160.300, F.A.C., any laboratory test required by this permit shall be performed by a laboratory that has been certified by the Department of Health Environmental Laboratory Certification Program (DOH ELCP).  Such certification shall be for the matrix, test method and analyte(s) being measured to comply with this permit.  For domestic wastewater facilities, testing for parameters listed in Rule 62-160.300(4), F.A.C., shall be conducted under the direction of a certified operator.

e.
Field activities including on-site tests and sample collection shall follow the applicable standard operating procedures described in DEP-SOP-001/01 adopted by reference in Chapter 62-160, F.A.C.  

f.
Alternate field procedures and laboratory methods may be used where they have been approved in accordance with Rules 62-160.220 and 62-160.330, F.A.C.

[62-620.610(18)]
19.
Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule detailed elsewhere in this permit shall be submitted no later than 14 days following each schedule date.  [62-620.610(19)]

20.
The permittee shall report to the Department any noncompliance which may endanger health or the environment.  Any information shall be provided orally within 24 hours from the time the permittee becomes aware of the circumstances.  A written submission shall also be provided within five days of the time the permittee becomes aware of the circumstances.  The written submission shall contain:  a description of the noncompliance and its cause; the period of noncompliance including exact dates and time, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.

a.
The following shall be included as information which must be reported within 24 hours under this condition:

1.
Any unanticipated bypass which causes any reclaimed water or effluent to exceed any permit limitation or results in an unpermitted discharge,

2.
Any upset which causes any reclaimed water or the effluent to exceed any limitation in the permit,

3.
Violation of a maximum daily discharge limitation for any of the pollutants specifically listed in the permit for such notice, and

4.
Any unauthorized discharge to surface or ground waters.

b.
Oral reports as required by this subsection shall be provided as follows:

1.
For unauthorized releases or spills of treated or untreated wastewater reported pursuant to subparagraph a.4 that are in excess of 1,000 gallons per incident, or where information indicates that public health or the environment will be endangered, oral reports shall be provided to the Department by calling the STATE WARNING POINT TOLL FREE NUMBER (800) 320-0519, as soon as practical, but no later than 24 hours from the time the permittee becomes aware of the discharge. The permittee, to the extent known, shall provide the following information to the State Warning Point:

a) Name, address, and telephone number of person reporting;

b) Name, address, and telephone number of permittee or responsible person for the discharge; 

c) Date and time of the discharge and status of discharge (ongoing or ceased); 

d) Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater);

e) Estimated amount of the discharge;

f) Location or address of the discharge; 

g) Source and cause of the discharge; 

h) Whether the discharge was contained on-site, and cleanup actions taken to date; 

i) Description of area affected by the discharge, including name of water body affected, if any; and  

j) Other persons or agencies contacted.

2.
Oral reports, not otherwise required to be provided pursuant to subparagraph b.1 above,  shall be provided to the Department within 24 hours from the time the permittee becomes aware of the circumstances. 

c.
If the oral report has been received within 24 hours, the noncompliance has been corrected, and the noncompliance did not endanger health or the environment, the Department shall waive the written report.


[62-620.610(20)]

21.
The permittee shall report all instances of noncompliance not reported under Permit Conditions IX. 17., 18. and 19. of this permit at the time monitoring reports are submitted.  This report shall contain the same information required by Permit Condition IX. 20 of this permit.  [62-620.610(21)]

22.
Bypass Provisions.

a.
Bypass is prohibited, and the Department may take enforcement action against a permittee for bypass, unless the permittee affirmatively demonstrates that:

1.
Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage; and 

2.
There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

3.
The permittee submitted notices as required under Permit Condition IX. 22. b. of this permit.

b.
If the permittee knows in advance of the need for a bypass, it shall submit prior notice to the Department, if possible at least 10 days before the date of the bypass.  The permittee shall submit notice of an unanticipated bypass within 24 hours of learning about the bypass as required in Permit Condition IX. 20. of this permit.  A notice shall include a description of the bypass and its cause; the period of the bypass, including exact dates and times; if the bypass has not been corrected, the anticipated time it is expected to continue; and the steps taken or planned to reduce, eliminate, and prevent  recurrence of the bypass.

c.
The Department shall approve an anticipated bypass, after considering its adverse effect, if the permittee demonstrates that it will meet the three conditions listed in Permit Condition IX. 22. a. 1. through 3. of this permit.

d.
A permittee may allow any bypass to occur which does not cause reclaimed water or effluent limitations to be exceeded if it is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of Permit Condition IX. 22. a. through c. of this permit.


[62-620.610(22)]

23.
Upset Provisions

a.
A permittee who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed contemporaneous operating logs, or other relevant evidence that:

1.
An upset occurred and that the permittee can identify the cause(s) of the upset;

2.
The permitted facility was at the time being properly operated;

3.
The permittee submitted notice of the upset as required in Permit Condition IX. 20. of this permit; and

4.
The permittee complied with any remedial measures required under Permit Condition IX. 5. of this permit.

b.
In any enforcement proceeding, the burden of proof for establishing the occurrence of an upset rests with the permittee.

c.
Before an enforcement proceeding is instituted, no representation made during the Department review of a claim that noncompliance was caused by an upset is final agency action subject to judicial review.

[62-620.610(23)]
Executed in Orlando, Florida.
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