AMENDMENT TO FACT SHEET

FOR

FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION

DOMESTIC WASTEWATER FACILITY PERMIT

	PERMIT NUMBER:
	FL0128937 (Major)

	FACILITY NAME:
	City of Clearwater Northeast AWWTF

	FACILITY LOCATION:
	Clearwater

Pinellas County

	NAME OF PERMITTEE:
	City of Clearwater

	PERMIT WRITER:
	Jeff Hilton, P.E.


1.
SYNOPSIS OF APPLICATION

a.
Chronology of Application

	
	Application Date:
	December 6, 2004

	
	Additional Information:
	February 1, 2005

	
	Public Notice Date:
	September 7, 2006



b.
Type of Facility


Domestic Wastewater Treatment Plant



Publicly-owned treatment works



Standard Industrial Classification Code: 4952


c.
Facility Capacity

	
	Existing Design Capacity:
	13.5
	MGD
	AADF

	
	Proposed Increase in Design Capacity:
	0
	MGD
	AADF

	
	Proposed Total Design Capacity:
	13.5
	MGD
	AADF


	
	Existing Permitted Capacity:
	13.5
	MGD
	AADF

	
	Proposed Increase in Permitted Capacity:
	0
	MGD
	AADF

	
	Proposed Total Permitted Capacity:
	13.5
	MGD
	AADF



d.
Description of Effluent or Reclaimed Water Discharges (as reported by applicant)
Outfall Serial Number D-001 

Annual Average Daily Flow (mgd): 13.5



pH Range (Standard Units): 6.5 to 8.5

The residuals description was updated.  

2.
BASIS FOR EFFLUENT AND RECLAIMED WATER LIMITS AND MONITORING REQUIREMENTS (INCLUDING EFFLUENT MONITORING REQUIREMENTS)
The following table and narrative provides amendments to the fact sheet for Part I. A. provisions.

The limits for Fecal Coliform and Toxicity where placed in the table.

The monitoring frequency for Dissolved Oxygen was changed from Daily to 7 Days/Week.  

The Nitrogen Load limit was removed from the table and the condition that related to this load limit was also removed.

Total Phosphorus and the Phosphorus Load were removed from the permit after the applicant provided the required information and the Department reviewed all the available data to make the determination that the receiving waterbody is Nitrogen limited and therefore the Facility qualifies for a Phosphorus Waiver under Department criteria. 

Outfall D-001 (Class III marine water):
	Parameter
	Limit
	Basis
	Rationale

	Whole Effluent Toxicity (Chronic) 
	100
	Single Sample Min.
	62-620.100(3)(j), 62-620.610(18), 62-620.620(1)(g) & 62-302.530(62), F.A.C


Whole Effluent Toxicity (Chronic) was mistakenly left out of the table in the original Fact Sheet.  The limit was added to the table, paragraph 8.b.2. the first sentence was changed to “A NOEC of less than 100% effluent in any routine test or additional test shall constitute a failure of the test.” and the last part of paragraph 8.f.5., “shall be terminated with the conclusion that the test constitutes non-compliance with these permit conditions.” was changed to “shall be terminated with the conclusion that the test failed.”  Additionally, the monitoring frequency has been reduced to Quarterly.  The facility has had 18 passing tests of the last 27, with 4 failures (5 invalids).  The Department finds that Quarterly monitoring is appropriate for this facility considering the past operational performance.  Reduction of monitoring frequency does not provide for a relaxation of effluent limitations.  Additionally, this permit does not allow for, nor does the Department find it appropriate, for this facility to further reduce monitoring frequency.

The sampling location for CBOD, TSS, TN, TP and pH have been moved from the plant site sampling location (EFA-01) to the Outfall sampling location (EFD-01) at the request of the City, on the basis that this location was more representative of the quality of the effluent being discharged. 

Ambient Monitoring: TSS was added to 9.d.(2). 

Total Coliform was removed from the Ambient Monitoring requirements.

The following narrative provides amendments to the fact sheet for Part I. B. provisions.

The limits for Fecal Coliform and Toxicity where placed in the table.

The monitoring frequency for TSS and fecal was change from Daily to 7 Days/Week. 

The following narrative provides amendments to the fact sheet for Part I. C. provisions.

#4 - The reference was added relating the monitoring of ground water discharges.

#9 – “except where grab samples are required by DEP SOP” was added to the second sentence for accuracy with the DEP SOP.

The following table provides amendments to the fact sheet for Part I. C. provisions.

Other Limitations and Monitoring Requirements:
	Parameter
	Limit
	Basis
	Rationale

	Rainfall (INCHES)
	Report
	Monthly Total 
	BPJ



It was clarified that Rainfall should be reported as a monthly total.


Influent sampling frequency was changed to weekly.  This is consistent with other major facilities.

The annual reuse report and reporting of storage were removed from this permit.  These are contained in the City’s Master Reuse Permit.

12.
APPLICABLE RULES
The following were used as the basis of the permit limitations/conditions:

	a.
FAC refers to various portions of the Florida Administrative Code.

The effective dates of FAC Rule Chapters cited in the table are as follows:

Chapter
Effective Date

62-4
05-01-03

62-160            04-09-02

62-302
05-15-02

62-520
12-09-96

62-522
08-27-01
62-550
05-28-03

62-600
12-24-96

62-601
12-24-96

62-602
02-06-02
62-610
08-08-99

62-620
08-25-03

62-625
01-08-97

62-640
03-30-98

62-650
12-26-96

62-699
07-05-01

b.
FS refers to various portions of the Florida Statutes

c.
CFR refers to various portions of the Code of Federal Regulations, Title 40

d.
BPJ refers to Best Professional Judgment

	


13.
DEPARTMENT CONTACT

Additional information concerning the permit may be obtained during normal business hours from:


Jeff Hilton, P.E.


Program Manager


Department's Southwest District Office


13051 N. Telecom Parkway 

Temple Terrace, FL 33637-0926


Telephone Number: 813-632-7600

Fax Number: 813-632-7662


jeff.hilton@dep.state.fl.us

14.
THE ADMINISTRATIVE RECORD
The administrative record including application, draft permit, fact sheet, amended fact sheet, public notice (after release), comments received and additional information is available for public inspection during normal business hours at the location specified in item 13.

15.
PROPOSED SCHEDULE FOR PERMIT ISSUANCE


	
	Draft permit to Applicant and EPA :
	May 3, 2006

	
	Beginning of Proposed Public Comment Period :
	September 7, 2006

	
	End of Proposed Public Comment Period :
	October 7, 2006

	
	Intent to Issue Permit:
	February 2, 2007

	
	Proposed Issuance Date of Permit :
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