     AMENDMENT TO FACT SHEET
FOR

STATE OF FLORIDA

DOMESTIC WASTEWATER FACILITY PERMIT

	PERMIT NUMBER:
	FL0026603 (Major)

	FACILITY NAME:
	City of Largo AWWTF

	FACILITY LOCATION:
	Clearwater

Pinellas County

	NAME OF PERMITTEE:
	City of Largo

	PERMIT WRITER:
	Jeff Hilton, P.E.


1.
SYNOPSIS OF APPLICATION

a.
Chronology of Application

	
	Application Date:
	September 9, 2004

	
	Additional Information:
	March 15, 2005

	
	Public Notice Date:
	September 16, 2006



b.
Type of Facility


Domestic Wastewater Treatment Plant



Publicly-owned treatment works



Standard Industrial Classification Code: 4952


c.
Facility Capacity

	
	Existing Design Capacity:
	18.0
	MGD
	AADF

	
	Proposed Increase in Design Capacity:
	0
	MGD
	AADF

	
	Proposed Total Design Capacity:
	18.0
	MGD
	AADF


	
	Existing Permitted Capacity:
	18.0
	MGD
	AADF

	
	Proposed Increase in Permitted Capacity:
	0
	MGD
	AADF

	
	Proposed Total Permitted Capacity:
	18.0
	MGD
	AADF



d.
Description of Effluent or Reclaimed Water Discharges (as reported by applicant)



See attached map(s) for the location(s) of effluent disposal and land application sites.

Outfall Serial Number D-001 

Annual Average Daily Flow (mgd): 18.0



pH Range (Standard Units): 6.5-8.0

 2.
BASIS FOR EFFLUENT AND RECLAIMED WATER LIMITS AND MONITORING REQUIREMENTS (INCLUDING EFFLUENT MONITORING REQUIREMENTS)
The following table and narrative provides amendments to the fact sheet for Part I. A. provisions.

The limit for Coliform, Fecal, % less than detection, was moved from the Annual Average column to the Monthly Average column where it belongs.
The monitoring frequency for Cyanide was changed from Monthly to Quarterly.  

The Nitrogen Load and Phosphorus Load limit was removed from the table and the condition that related to these load limits was also removed.

	Parameter
	Limit
	Basis
	Rationale

	Oxygen, Dissolved  (DO) (MG/L)
	5.0
	Single Sample Min.
	62-302.530(31) FAC

	Whole Effluent Toxicity (Chronic) 
	100
	Single Sample Min.
	62-620.100(3)(j), 62-620.610(18), 62-620.620(1)(g) & 62-302.530(62), F.A.C


Dissolved Oxygen was mistakenly left out of the Table.

Whole Effluent Toxicity (Chronic), additional references were added to the rationale.
Total Coliform was removed from the Ambient Monitoring requirements.

The following narrative provides amendments to the fact sheet for Part I. B. provisions.

The limit for Coliform, Fecal, % less than detection, was moved from the Annual Average column to the Monthly Average column where it belongs.

The following narrative provides amendments to the fact sheet for Part I. C. provisions.

#3 - Influent sampling was changed to “ Influent samples shall be collected so that less than ten percent of the total flow is attributed to digester supernatant or return activated sludge, or any other plant process recycled waters.”, due to physical restraints at the facility.
#8 - The reference was added relating to the monitoring of ground water discharges.

#12 – “except where grab samples are required by DEP SOP” was added to the second sentence for accuracy with the DEP SOP.

The following narrative provides amendments to the fact sheet for Part III provisions.
The monitoring wells at Feather Sound were removed form the permit since reclaimed water is no long applied there.

The Sample Type for Turbidity was changed to correct type, In-Situ.
12.
APPLICABLE RULES
The following were used as the basis of the permit limitations/conditions:

	a.
FAC refers to various portions of the Florida Administrative Code.

The effective dates of FAC Rule Chapters cited in the table are as follows:

Chapter
Effective Date

62-4
05-01-03

62-160            04-09-02

62-302
05-15-02

62-520
12-09-96

62-522
08-27-01
62-550
05-28-03

62-600
12-24-96

62-601
12-24-96

62-602
02-06-02
62-610
08-08-99

62-620
08-25-03

62-625
01-08-97

62-640
03-30-98

62-650
12-26-96

62-699
07-05-01

b.
FS refers to various portions of the Florida Statutes

c.
CFR refers to various portions of the Code of Federal Regulations, Title 40

d.
BPJ refers to Best Professional Judgment

	


13.
DEPARTMENT CONTACT

Additional information concerning the permit may be obtained during normal business hours from:


Jeff Hilton, P.E.


DW Program Manager


Department's Southwest District Office


13051 N. Telecom Parkway, 

Temple Terrace, FL, FL 33637 - 0926


Telephone Number: 813-632-7600

Fax Number: 813-632-7662


jeff.hilton@dep.state.fl.us

14.
THE ADMINISTRATIVE RECORD
The administrative record including application, draft permit, fact sheet, public notice (after release), comments received and additional information is available for public inspection during normal business hours at the location specified in item 13.

15.
PROPOSED SCHEDULE FOR PERMIT ISSUANCE
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