FACT SHEET


FOR


STATE OF FLORIDA


DOMESTIC WASTEWATER FACILITY PERMIT





PERMIT NUMBER:�
FL0041441 (Major)�
�
FACILITY NAME:�
City of Venice East Side AWWTF�
�
FACILITY LOCATION:�
Venice


Sarasota County�
�
NAME OF PERMITTEE:�
City of Venice�
�
PERMIT WRITER:�
Jeff Hilton, P.E.�
�



1.	SYNOPSIS OF APPLICATION


	a.	Chronology of Application


�
Application Date:�
October 22, 2004�
�
�
Additional Information:�
December 17, 2004�
�
�
Public Notice Date:�
�
�
	b.	Type of Facility


		Domestic Wastewater Treatment Plant


		Publicly-owned treatment works


		Standard Industrial Classification Code: 4952


	c.	Facility Capacity


�
Existing Design Capacity:�
6.0�
MGD�
TMADF�
�
�
Proposed Increase in Design Capacity:�
0�
MGD�
TMADF�
�
�
Proposed Total Design Capacity:�
6.0�
MGD�
TMADF�
�



�
Existing Permitted Capacity:�
6.0�
MGD�
TMADF�
�
�
Proposed Increase in Permitted Capacity:�
0�
MGD�
TMADF�
�
�
Proposed Total Permitted Capacity:�
6.0�
MGD�
TMADF�
�



	d.	Description of Effluent or Reclaimed Water Discharges (as reported by applicant)


		


Outfall Serial Number D-001  3.0 AADF


		pH Range (Standard Units): 6.0-8.5 (Existing permits)

















Pollutants which are present in significant quantities or which are subject to effluent or reclaimed water limitations are as follows:


Parameters�
Reported Data�
�
 �
Annual Avg.�
Lowest Monthly Avg.�
Highest Monthly Avg.�
�
Flow, Total Plant (through 2004)�
2.384�
1.986�
2.693�
�






Parameters�
Reported Data�
�
 �
Annual Avg.�
Lowest Monthly Avg.�
Highest Monthly Avg.�
�
pH�
-�
6.5�
7.9�
�
Fecal Coliform�
<1.0�
-�
<1.0�
�
CBOD5�
2.3�
1.6�
3.6�
�
Total Suspended Solids�
0.733�
-�
3.8�
�
Total Nitrogen*�
2.3�
- �
3.7�
�
Total Phosphorous�
0.2�
-�
0.6�
�
Total Residual Chlorine (Disinfection)�
1.6�
1.5�
1.8�
�
Total Residual Chlorine (Dechlorination)�
<0.01�
<0.01�
<0.2�
�
Dissolved Oxygen�
7.5�
-�
8.7�
�
* A twelve (12) month rolling average Total Nitrogen loading is established to maintain the current permitted nutrient loading limits and shall not exceed 6370 lbs per year Outfall Serial Number D-001


2.	BASIS FOR EFFLUENT AND RECLAIMED WATER LIMITS AND MONITORING REQUIREMENTS (INCLUDING EFFLUENT MONITORING REQUIREMENTS)


The following table provides the basis for Part I. A. provisions.


Outfall D-001 (Class III fresh water):


Parameter�
Limit�
Basis�
Rationale�
�
Flow (D-001) (MGD)�
Report�3.0�
Monthly Average�Annual Average�
BPJ�62-600.400(3)(b) FAC�
�
Flow(Curry Creek) (CFS)�
47.0�
Single Sample Min.�
BPJ�
�
BOD, Carbonaceous  5 day, 20C (MG/L)�
5.0�


6.25�7.5�10.0�
Annual Average�


Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)1. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�


6.25�7.5�10.0�
Annual Average�


Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)2. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Nitrogen, Total (as N) (MG/L)�
3.0�


3.75�4.5�6.0�
Annual Average�


Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)3. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Phosphorus, Total  (as P) (MG/L)�
1.0�


1.25�1.5�2.0�
Annual Average�


Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)4. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�
Single Sample Max.�
62-600.440(5)(e). FAC�
�
pH (SU)�
6.0 to 8.5�
Minimum and Maximum�
62-302.530(52) FAC�
�
Oxygen, Dissolved  (DO) (MG/L)�
7.0�
Single Sample Min.�
BPJ�
�
Coliform, Fecal, % less than detection (PERCENT)�
75�
Minimum�
62-600.440(5)(f)1. FAC�
�
Coliform, Fecal (#/100ML)�
25�
Single Sample Max.�
62-600.440(5)(f)2. FAC�
�
Total Residual Chlorine (For Disinfection) (MG/L)�
1.0�
Minimum�
62-600.440(5)(b) FAC�
�
Total Residual Chlorine (For Dechlorination) (MG/L)�
0.01�
Single Sample Max.�
62-600.440(2)  FAC & 62-302.530(19) FAC�
�
Chlorodibromomethane (UG/L)�
34.0�
Annual Average�
62-302.530(36)�
�
Dichlorobromomethane (UG/L)�
22.0�
Annual Average�
62-302.530(36)�
�
Whole Effluent Toxicity (Chronic) (***)�
100�
Single Sample Min.�
62-302.530(21) & (62) FAC�
�
Flow in Curry Creek and the DO limit are based on previous sampling conducted to justify the increase in the discharge.


The following table provides the basis for Part I. B. provisions.


Land Application System R-001 (slow-rate public access):


Parameter�
Limit�
Basis�
Rationale�
�
Flow (R-001) (MGD)� �
2.0�
Annual Average�
62-600.400(3)(b) & 62-610.810(5) FAC�
�
BOD, Carbonaceous  5 day, 20C (MG/L)�
20.0�30.0�45.0�60.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
62-610.460 & 62-600.740(1)(b)1.a. FAC�62-600.740(1)(b)1.b. FAC�62-600.740(1)(b)1.c. FAC�62-600.740(1)(b)1.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�
Single Sample Max.�
62-610.460(1) & 62-600.440(5)(f)3. FAC�
�
pH (SU)�
6.0 to 8.5�
Minimum and Maximum�
62-600.445 FAC�
�
Coliform, Fecal, % less than detection (PERCENT)�
75�
Minimum�
62-600.440(5)(f)1. FAC�
�
Coliform, Fecal (#/100ML)�
25�
Single Sample Max.�
62-610.460 & 62-600.440(5)(f)2. FAC�
�
Total Residual Chlorine (For Disinfection) (MG/L)�
1.0�
Minimum�
62-600.440(5(b), 62-610.460(2), &  62-610.463(2) FAC�
�
Turbidity (NTU)�
Report�
Single Sample Max.�
62-610.463(2) FAC�
�
Giardia (CYSTS/100 L)�
Report�
Single Sample Max.�
62-610.463(4) FAC�
�
Cryptosporidium (OOCYSTS/100 L)�
Report�
Single Sample Max.�
62-610.463(4) FAC�
�



Land Application System R-002 (slow-rate public access):


Parameter�
Limit�
Basis�
Rationale�
�
Flow (R-002) (MGD)� �
2.5�
Annual Average�
62-600.400(3)(b) & 62-610.810(5) FAC�
�
BOD, Carbonaceous  5 day, 20C (MG/L)�
20.0�30.0�45.0�60.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
62-610.460 & 62-600.740(1)(b)1.a. FAC�62-600.740(1)(b)1.b. FAC�62-600.740(1)(b)1.c. FAC�62-600.740(1)(b)1.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�
Single Sample Max.�
62-610.460(1) & 62-600.440(5)(f)3. FAC�
�
pH (SU)�
6.0 to 8.5�
Minimum and Maximum�
62-600.445 FAC�
�
Coliform, Fecal, % less than detection (PERCENT)�
75�
Minimum�
62-600.440(5)(f)1. FAC�
�
Coliform, Fecal (#/100ML)�
25�
Single Sample Max.�
62-610.460 & 62-600.440(5)(f)2. FAC�
�
Total Residual Chlorine (For Disinfection) (MG/L)�
1.0�
Minimum�
62-600.440(5(b), 62-610.460(2), &  62-610.463(2) FAC�
�
Turbidity (NTU)�
Report�
Single Sample Max.�
62-610.463(2) FAC�
�
Giardia (CYSTS/100 L)�
Report�
Single Sample Max.�
62-610.463(4) FAC�
�
Cryptosporidium (OOCYSTS/100 L)�
Report�
Single Sample Max.�
62-610.463(4) FAC�
�



The following table provides the basis for Part I. C. provisions.


Internal Outfall R-003 


Dissolved Oxygen, Total Residual Chlorine (For Dechlorination) and Toxicity are monitored under the Industrial Wastewater Permit, FL00035335.


Parameter�
Limit�
Basis�
Rationale�
�
Flow (R-003) (MGD)�
Report�1.0�
Monthly Average�Annual Average�
BPJ�62-600.400(3)(b) FAC�
�
BOD, Carbonaceous  5 day, 20C (MG/L)�
5.0�6.25�7.5�10.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)1. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�6.25�7.5�10.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)2. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Nitrogen, Total (as N) (MG/L)�
3.0�3.75�4.5�6.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)3. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Phosphorus, Total  (as P) (MG/L)�
1.0�1.25�1.5�2.0�
Annual Average�Monthly Average�Weekly Average�Single Sample Max.�
403.086(4)(a)4. FS & 62-600.740(1)(b)2.a. FAC�62-600.740(1)(b)2.b. FAC�62-600.740(1)(b)2.c. FAC�62-600.740(1)(b)2.d. FAC�
�
Solids, Total  Suspended (MG/L)�
5.0�
Single Sample Max.�
62-600.440(5)(e). FAC�
�
pH (SU)�
6.0 to 8.5�
Minimum and Maximum�
62-302.530(52) FAC�
�
Coliform, Fecal, % less than detection (PERCENT)�
75�
Minimum�
62-600.440(5)(f)1. FAC�
�
Coliform, Fecal (#/100ML)�
25�
Single Sample Max.�
62-600.440(5)(f)2. FAC�
�
Total Residual Chlorine (For Disinfection) (MG/L)�
1.0�
Minimum�
62-600.440(5)(b) FAC�
�
Chlorodibromomethane (UG/L)�
34.0�
Annual Average�
62-302.530(36)�
�
Dichlorobromomethane (UG/L)�
22.0�
Annual Average�
62-302.530(36)�
�
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The following table provides the basis for Part I. D. provisions.


Other Limitations and Monitoring Requirements:


Parameter�
Limit�
Basis�
Rationale�
�
Flow (MGD)�
6.0�
Annual Average�
62-600.400(3)(b)FAC�
�
Percent Capacity, (TMADF/Permitted Capacity) x 100 (PERCENT)�
Report�
Monthly Average�
62-600.405(4) FAC�
�
BOD, Carbonaceous  5 day, 20C (MG/L)�
Report�
Monthly Average�
62-601.300(1)FAC�
�
Solids, Total  Suspended (MG/L)�
Report�
Monthly Average�
62-601.300(1)FAC�
�
Rainfall (INCHES)�
Report�
Monthly Average�
BPJ�
�
Monitoring Frequency and Sample Type�
-�
All Parameters�
62-601 FAC & 62-699 FAC and/or BPJ of permit writer�
�
Sampling Location�
-�
All Parameters�
62-601, 62-610.412, 62-610.463(1), 62-610.568, 62-610.613 FAC and/or BPJ of permit writer�
�



	Rainfall is being included in all major permits where a public assess reuse system is utilized.


3.	RESIDUALS MANAGEMENT


The method of residuals use or disposal by this facility are transport to RMF, or disposal in a Class I or II solid waste landfill.


4.	GROUND WATER MONITORING REQUIREMENTS


Ground water monitoring requirements have been established in accordance with Rules 62-601 and 62-522, F.A.C. 


5.	SCHEDULES FOR IMPROVEMENT ACTIONS, CONSTRUCTION, AND ENGINEERING STUDIES


The following improvement actions shall be completed according to the following schedule:


�
Improvement Action�
Completion Date�
�
�
1�
Submit to the Department a proposed Ground Water Monitoring Plan for the City of Venice Master Reuse System in accordance with 62-522.600�
Within 90 days of permit issuance�
�



6.	INDUSTRIAL PRETREATMENT REQUIREMENTS


After a review of the facilities comments and in accordance with 62-625.200(20)(c) and 62-625.500(2)(e), this section is not applicable to this facility.





7.	ADMINISTRIATIVE ORDERS (AO) AND CONSENT ORDERS (CO)


This permit is not accompanied by an AO, and there are no unresolved compliance issues for this facility.


8.	REQUESTED VARIANCES OR ALTERNATIVES TO REQUIRED STANDARDS


No variances were requested for this facility. 


9.	DISCUSSION OF PREVIOUS PERMIT EFFLUENT OR RECLAIMED WATER LIMITATIONS.


	All of the past effluent limits and reclaimed water limits are present in this permit. 


10.	NEW OR EXPANDED DISCHARGES TO SURFACE WATERS; ANTIDEGRADATION REQUIREMENTS


This facility does not have a new or expanded discharge.


11.	EFFECTS OF SURFACE WATER DISCHARGE ON THREATENED OR ENDANGERED SPECIES


The Department does not anticipate adverse impacts on threatened or endangered species as a result of permit issuance.


12.	APPLICABLE RULES


The following were used as the basis of the permit limitations/conditions:


a.	FAC refers to various portions of the Florida Administrative Code.


The effective dates of FAC Rule Chapters cited in the table are as follows:


Chapter	Effective Date


62-4	05-01-03


62-160            04-09-02


62-302	05-15-02


62-520	12-09-96


62-522	08-27-01


62-550	05-28-03


62-600	12-24-96


62-601	12-24-96


62-602	02-06-02


62-610	08-08-99


62-620	08-25-03


62-625	01-08-97


62-640	03-30-98


62-650	12-26-96


62-699	07-05-01


b.	FS refers to various portions of the Florida Statutes


c.	CFR refers to various portions of the Code of Federal Regulations, Title 40


d.	BPJ refers to Best Professional Judgment�
�
�
�



13.	DEPARTMENT CONTACT


Additional information concerning the permit may be obtained during normal business hours from:


	Jeff Hilton, P.E.


	Department's Southwest District Office


	13051 N. Telecom Parkway


	Temple Terrace, FL, FL 33637-0926


	Telephone Number: 813-632-7600


	Fax Number: 813-632-7662


14.	THE ADMINISTRATIVE RECORD


The administrative record including application, draft permit, fact sheet, public notice (after release), comments received and additional information is available for public inspection during normal business hours at the location specified in item 13.


15.	PROPOSED SCHEDULE FOR PERMIT ISSUANCE


	Draft Permit Issued					April 14, 2006


	Beginning of Proposed Comment Period:			May 4, 2006


	End of Proposed Public Comment Period:			June 4, 2006


	Proposed permit to EPA:					April 14, 2006


	Notice of Agency Action:					August 16, 2006


	Proposed Issuance Date of Permit:				August 18, 2006














� City of Venice Master Reuse System


� Sarasota County South Master Reuse System
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