	FACILITY:
	William E. Dunn WRF
	PERMIT NUMBER:
	FL0128775

	PERMITTEE:
	Pinellas County Utilities
	
	



	[image: image1.png]



	Florida Department of

Environmental Protection

Southwest District Office

13051 North Telecom Parkway

Temple Terrace, Florida  33637-0926


	Charlie Crist

Governor

Jeff Kottkamp
Lt. Governor

Michael W. Sole

Secretary


STATE OF FLORIDA

DOMESTIC WASTEWATER FACILITY PERMIT

	PERMITTEE:
	PERMIT NUMBER:
	FL0128775 

	
	PA FILE NUMBER:
	FL0128775-009-DW1P/NR

	Pinellas County Utilities
	ISSUANCE DATE:
	January 27, 2010

	
	EXPIRATION DATE:
	January 26, 2015

	RESPONSIBLE AUTHORITY:
	
	

	
	
	

	Mr. James R. Rolston

	Director of Utilities Operations

	1620 Ridge Road, Building A

	Largo, FL 33778

jrolston@pinellascounty.org


(727) 582-2300
FACILITY:

	William E. Dunn WRF

	4111 Dunn Drive

	Palm Harbor, FL  34683

	Pinellas County
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This permit is issued under the provisions of Chapter 403, Florida Statutes (F.S.), and applicable rules of the Florida Administrative Code (F.A.C.) and constitutes authorization to discharge to waters of the state under the National Pollutant Discharge Elimination System.  The above named permittee is hereby authorized to operate the facilities shown on the application and other documents attached hereto or on file with the Department and made a part hereof and specifically described as follows:

TREATMENT FACILITIES:

Operation of an existing 9.0 million gallons per day (MGD) annual average daily flow (AADF) Type I, five-stage Bardenpho activated sludge, advanced domestic wastewater treatment plant consisting of: headworks with mechanical screening and induced vortex grit removal; two parallel Bardenpho trains consisting of two fermentation basins of 0.76 million gallons (MG) total volume, two first anoxic basins of 1.69 MG total volume, three oxidation reactors of 5.81 MG total volume, two second anoxic basins of 1.88 MG total volume, and two re-aeration basins of 0.22 MG total volume; six final clarifiers of 3.6 MG total volume and 30,600 ft2 total surface area; four automatic backwash filters of 3,200 ft2 total surface area; and two chlorine contact chambers of 0.325 MG total volume.

The residuals handling components consist of two aerated sludge holding tanks of 0.44 MG total volume and two belt filter presses.  Residuals are transported to a permitted Residuals Management Facility for further treatment and disposal.

The plant is a dual train facility with the exception of the headworks.  Filter backwash and belt filter press washwater are returned to the headworks downstream of flow measurement and sampling.  Alum and/or polymer feed are available on a standby status for solids control and polymer is available for the residuals handling processes.  Effluent quality is continuously monitored for turbidity as a measure of TSS and chlorine residual as a measure of disinfection effectiveness.  Two autostart standby generators (1,000 KW each) are available as an alternative power source.

Effluent failing to meet Part III public access quality standards is directed by means of an automatic valve system to a lined reject storage pond of 17 MG total volume.  Effluent which does meet Part III quality standards is stored on site in a lined reclaimed water storage pond of 64 MG total volume.  The on-site storage is controlled, sequenced and operated according to procedures set forth in the plant Operating Protocol in order to assure maximum reliability and safeguards on the quality of the reclaimed water.  The Part III reclaimed water is transferred to the Northwest Pinellas Master Reuse System (R-001) as described below. 
REUSE:

Land Application:  An existing 9.0 MGD annual average daily flow (AADF) permitted capacity slow-rate Part III public access (R-001) as defined on the map entitled "North Pinellas County Reclaimed Water Master Plan", undated, prepared by Camp Dresser & McKee, Inc.  The reuse system generally located in northern Pinellas County and is composed primarily of spray irrigation of golf courses, common areas, residential subdivisions, parks, schools, athletic facilities and various other public and private parcels.  The master reuse system existing and potential users are listed in Section IV of this permit.  In addition to storage of reclaimed water as described above, reclaimed water is also diurnally stored in irrigation lakes at Innisbrook Highlands and Copperhead Golf Courses, Tarpon Woods Golf Course, East Lake Woodlands Golf Course, and Highlands Lakes Red Golf Course, as described below.
Intermittently discharging stormwater storage ponds for Part III Reclaimed Water:

Reclaimed water is stored in a stormwater storage lake system at Highlands of Innisbrook Golf Course, identified by monitoring group number D-001 and monitoring location number STM-01.  STM-01 may intermittently discharge through a control structure during storm events to a wetlands and ultimately to St. Joseph Sound.  STM-01 is located at approximately latitude 28º 06' 15" N, longitude 82º 45' 27" W.
Reclaimed water is stored in two stormwater storage lake systems at Copperhead Golf Course, identified by monitoring group numbers D-002 and D-003 and monitoring location numbers STM-02 and STM-03 respectively. STM-02 and STM-03 may intermittently discharge through control structures during storm events to a wetlands and ultimately to St. Joseph Sound.  STM-02 and STM-03 are located at approximately latitude 28º 06' 40" N, longitude 82º 45' 07" W.
Reclaimed water is stored in two stormwater storage lake systems at Tarpon Woods Golf Course, identified by monitoring group numbers D-004 and D-005 and monitoring location numbers STM-04 and STM-05 respectively. STM-04 and STM-05 may intermittently discharge through control structures during storm events to a wetlands and ultimately to Brooker Creek.  STM-04 and STM-05 are located at approximately latitude 28º 05' 22" N, longitude 82º 40' 29" W.  
Reclaimed water is stored in two stormwater storage lake systems at East Lake Woodlands Golf Course, identified by monitoring group numbers D-006 and D-007 and monitoring location numbers STM-06 and STM-07 respectively.  STM-06 and STM-07 may intermittently discharge through control structures during storm events to a wetlands and ultimately to Brooker Creek.  STM-06 and STM-07are located at approximately latitude 28º 04' 36" N, longitude 82º 41' 15" W.  
Reclaimed water is stored in a stormwater storage lake system at Highland Lakes Red Golf Course, identified by monitoring group number D-008 and monitoring location number STM-08.  STM-08 may intermittently discharge through a control structure during storm events to a wetlands and ultimately to Lake Tarpon.  STM-08 is located at approximately latitude 28º 04' 46" N, longitude 82º 41' 02".
Reclaimed water meeting Part III Public Access standards is provided by two existing separately permitted wastewater treatment facilities as follows:

City of Clearwater – up to 3.0 MGD AADF


City of Oldsmar – up to 0.800 MGD AADF

Effluent quality is continuously monitored at the source wastewater treatment plants for high level disinfection in accordance with each facility’s approved operating protocol.  For all source plants, the on-site and off-site storage is controlled, sequenced, and operated during staffed and unstaffed periods according to procedures set forth in an Operating Protocol established for each source plant in order to assure maximum reliability and safeguards on the quality of the reclaimed water.  All source reclaimed waters to the public access master reuse system, R-001, are limited to 9.0 MGD AADF.  Supplemental water is used to meet reuse demands when the facility and its contributors are unable to supply 9.0 MGD.
The reuse system R-001 is allowed to receive surface water from the following: An existing 1.0 MGD annual average daily flow (AADF) permitted capacity  Lake Tarpon Supplemental Water System which has an in-lake intake system (cylindrical intake screen), a pump station, a filtration system (pre-filter and second filter) with filter flush pump tank and piping to the existing sewer force main, a deoxygenating system (membrane contactors with available nitrogen sweep) for DO reduction, UV Disinfection (two chambers), and a ASR well (designated as Monitoring Group Number I-001 and permitted under Department Permit No: 231277-001-UC for 1.0 MGD of recharge/recovery).  This system will provide supplemental water for the public access reuse system from treated water from the ASR well or from treated water directly from Lake Tarpon by blending the recovered water into the public access reclaimed water distribution system. 
IN ACCORDANCE WITH: The limitations, monitoring requirements and other conditions set forth in Pages 1 through 27 of this permit.

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.
Reuse and Land Application Systems

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to direct reclaimed water to Reuse System R-001.  Such reclaimed water shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.B.7:

	 
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (Total reclaimed water to R-001)
	MGD
	Maximum
	9.0
	Report
	-
	-
	Monthly
	Calculation
	FLW-05
	See Cond.I.A.4

	Flow (from William E. Dunn)
	MGD
	Maximum
	9.0
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-02
	See Cond.I.A.4

	Flow ( from City of Clearwater)
	MGD
	Maximum
	3.0
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-03
	See Cond.I.A.4

	Flow (from City of Oldsmar)
	MGD
	Maximum
	0.8
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-04
	See Cond.I.A.4

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	20.0
	30.0
	45.0
	60.0
	5 Days/Week
	24-hour flow proportioned composite
	EFA-01
	

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	-
	-
	5.0
	7 Days/Week
	Grab
	EFB-01
	

	pH
	SU
	Range
	-
	-
	-
	6.0 to 8.5
	Continuous
	Meter
	EFA-01
	See Cond.I.A.3

	Coliform, Fecal, % less than detection
	PERCENT
	Minimum
	-
	75
	-
	-
	Monthly
	Calculation
	EFA-01
	See

Cond. I.A.5.

	Coliform, Fecal
	#/100ML
	Maximum
	-
	-
	-
	25
	7 Days/Week
	Grab
	EFA-01
	See

Cond. I.A.5.

	Total Residual Chlorine (For Disinfection)
	MG/L
	Minimum
	-
	-
	-
	1.0
	Continuous
	Meter
	EFA-01
	See Cond.I.A.6

	Turbidity
	NTU
	Maximum
	
	
	
	Report
	Continuous
	Meter
	EFB-01
	See 

Cond. I.A.7.

	Nitrogen, Total (as N)
	MG/L
	Maximum
	-
	Report
	-
	Report
	Monthly
	24-hour flow proportioned composite
	EFA-01
	

	Phosphorus, Total  (as P)
	MG/L
	Maximum
	-
	Report
	-
	Report
	Monthly
	24-hour flow proportioned composite
	EFA-01
	

	Giardia
	CYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-01
	See Cond.I.A.10

	Cryptosporidium
	OOCYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFA-01
	See Cond.I.A.10


2. Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I.A.1 and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	EFA-01
	After disinfection and prior to the public access reuse system (R-001).

	EFB-01
	After filtration and prior to disinfection.

	FLW-02
	Flow as measured at the public access reuse pump station.

	FLW-03
	Flow as measured prior to the ground storage tank accepting reclaimed source water from the City of Clearwater.

	FLW-04
	Flow as measured prior to the ground storage tank accepting reclaimed source water from the City of Oldsmar.

	FLW-05
	Total Public Access Reuse water measured by summing FLW-02, FLW-03, and FLW-04.


3. Hourly measurement of pH during the period of required operator attendance may be substituted for continuous measurement.  [Chapter 62-601, Figure 2]  

4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.  Note:  To report the “% less than detection,” count the number of fecal coliform observations that were less than detection, divide by the total number of fecal coliform observations in the month, and multiply by 100% (round to the nearest integer).  [62-600.440(5)(f)]  

6. The minimum total chlorine residual shall be limited as described in the approved operating protocol, such that the permit limitation for fecal coliform bacteria will be achieved.  In no case shall the total chlorine residual be less than 1.0 mg/L.  [62-600.440(5)(b); 62-610.460(2); and 62-610.463(2)]  

7. The maximum turbidity shall be limited as described in the approved operating protocol, such that the permit limitations for total suspended solids and fecal coliforms will be achieved.  [62-610.463(2)]  
8. The treatment facilities shall be operated in accordance with all approved operating protocols.  Only reclaimed water that meets the criteria established in the approved operating protocols may be released to system storage or to the reuse system.  Reclaimed water that fails to meet the criteria in the approved operating protocols shall be directed to reject storage for subsequent additional treatment or disinfection.  The operating protocols shall be reviewed and updated periodically to ensure continuous compliance with the minimum treatment and disinfection requirements.  Updated operating protocols shall be submitted to the Department for review and approval upon revision of the operating protocols and with each permit application.  [62-610.320(6) and 62-610.463(2)]  

9. Instruments for continuous on-line monitoring of total residual chlorine and turbidity shall be equipped with an automated data logging or recording device.  [62-610.463(2) & .865(8)(d)]
10. Intervals between sampling for Giardia and Cryptosporidium shall not exceed two years.  Sampling results shall be reported on DEP Form 62-610.300(4)(a)4 which is attached to this permit.  (If additional sampling is required in accordance with the attached form, only one additional sampling event will be required within the two year monitoring frequency)  This form shall be submitted to the Department and to DEP’s Reuse Coordinator in Tallahassee.  [62-610.463(4)]
11. Delivery of reclaimed water to the lakes listed in the table below shall only occur when the elevations of the water in the lakes are less than the corresponding control elevation listed in the table below.  A list of all days during a month on which discharges from the lakes to the receiving water bodies occurred shall be attached to the DMR form.  For each day on which discharge occurred, the approximate number of hours of discharge shall be noted. [62-610.830(1) and (3)] 
	Monitoring Location Site Number
	Name of Storage Lake/Description of Monitoring Location
	Control Elevation (ft. M.S.L.)
	Receiving Water Body

	STM-01
	Highlands of Innisbrook GC (D-001)
	4.75
	St. Joseph Sound

	STM-02
	Copperhead GC Back 9 Lake (D-002)
	5.19
	St. Joseph Sound

	STM-03
	Copperhead GC Front 9 Lake (D-003)
	4.23
	St. Joseph Sound

	STM-04
	Tarpon Woods Driving Range Lake (D-004)
	6.48
	Brooker Creek

	STM-05
	Tarpon Woods Back Pond (D-005)
	7.45
	Brooker Creek

	STM-06
	East Lake Woodlands North Pond (D-006)
	7.19
	Brooker Creek

	STM-07
	East Lake Woodlands Maintenance Area Pond (D-007)
	7.93
	Brooker Creek

	STM-08
	Highland Lakes Red Golf Course (D-008)
	19.74
	Lake Tarpon 


12. During the period beginning on the date of Department approval to place the system into operation and lasting through the expiration date of this permit, when the system is operational, the permittee is authorized to direct supplemental water from I-001 to Reuse System R-001.  Such supplemental water shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.B.7:

	 
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (from Lake Tarpon to ASR system)
	MGD
	Maximum
	1.0
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-06
	See Cond.I.A.14

	Flow (from ASR system to R-001)
	MGD
	Maximum
	Report
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-07
	See Cond.I.A.14

	Flow (from Lake Tarpon to R-001)
	MGD
	Maximum
	Report
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-08
	See Cond.I.A.14

	Coliform, Fecal, % less than detection
	PERCENT
	Minimum
	-
	75
	-
	-
	Monthly
	Calculation
	EFF-02
	See

 Cond. I.A.15.

	Coliform, Fecal (from ASR system)
	#/100ML
	Maximum
	-
	-
	-
	25
	7 Days/Week
	Grab
	EFF-02
	See

 Cond. I.A.15.

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	-
	-
	5.0
	7 Days/Week
	Grab
	EFF-02
	

	Conductance, Specific (from ASR system)
	UMHO/CM
	Maximum
	-
	-
	-
	Report
	Weekly
	Grab
	EFF-02
	

	Solids, Total Dissolved (TDS)
	MG/L
	Maximum
	-
	-
	-
	Report
	Weekly
	Grab
	EFF-02
	

	Chloride (as Cl)
	MG/L
	Maximum
	-
	-
	-
	Report
	Weekly
	Grab
	EFF-02
	

	Arsenic, Total Recoverable
	UG/L
	Maximum
	-
	-
	-
	Report
	Weekly
	Grab
	EFF-02
	

	Ultraviolet Light  Dosage
	MW-S/CM2
	Minimum
	-
	-
	-
	50
	Continuous
	Meter
	EFF-01
	See

 Cond. I.A.17.

	Ultraviolet Light Transmittance
	PERCENT
	Maximum
	-
	-
	-
	50
	Continuous
	Meter
	EFF-01
	See

 Cond. I.A.16.

	Ultraviolet Light Intensity
	UW/CM2
	Maximum
	-
	-
	-
	Report
	Continuous
	Meter
	EFF-01
	See

 Cond. I.A.18.

	Giardia
	CYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFF-02
	See Cond.I.A.10

	Cryptosporidium
	OOCYSTS/100 L
	Maximum
	-
	-
	-
	Report
	two years
	Filtered
	EFF-02
	See Cond.I.A.10


13. Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I. A.  13. and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	I-001
	Monitoring Group Number for the supplemental water.

	EFF-01
	After filter and prior to ASR Well.

	EFF-02
	After ASR Well or directly from Lake Tarpon and prior to R-001.

	FLW-06
	Flow from Lake Tarpon to ASR Well.

	FLW-07
	Flow from ASR Well to R-001.

	FLW-08
	Flow from Lake Tarpon directly to R-001.


14. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

15. Over a 30-day period, at least 75 percent of the fecal coliform values shall be below the detection limits.  No sample shall exceed 25 fecal coliforms per 100 mL.  No sample shall exceed 5.0 mg/L of total suspended solids (TSS) at a point before the application of the disinfectant.    [62-600.440(5)(f)] 
16. UV transmittance shall be monitored and logged continuously, and shall be limited as described in the approved operating protocol. [62-600.440(1); 62-4.070; 62-610.463(2)]
17. Operational UV dosage shall be continuously calculated and logged and shall be limited as described in the approved operating protocol. [62-600.440(1); 62-4.070; 62-610.463(2)]
18. UV intensity shall be monitored and logged continuously in each reactor.  The location of the probe shall be at the point as was used in the validation testing of the UV unit. [62-600.440(1); 62-4.070; 62-610.463(2)]
19. The filtration and UV disinfection systems shall be operated in compliance with the approved operating protocol, such that the permit limitations for fecal coliform bacteria shall be achieved.  [62-600.440(5)(b); 62-610.460(2); 62-610.463(2)] 

B.
Other Limitations and Monitoring and Reporting Requirements

1. During the period beginning on the issuance date and lasting through the expiration date of this permit, the treatment facility shall be limited and monitored by the permittee as specified below and reported in accordance with condition I.B.7:

	
	
	
	Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow, Total Plant
	MGD
	Maximum
	9.0
	Report
	-
	-
	Continuous
	Recording flow meters and totalizers
	FLW-01
	See Cond.I.B.4

	Percent Capacity, (3MRADF/Permitted Capacity) x 100
	PERCENT
	Maximum
	-
	Report
	-
	-
	Monthly
	Calculation
	FLW-01
	

	BOD, Carbonaceous  5 day, 20C
	MG/L
	Maximum
	-
	Report
	-
	-
	Weekly
	24-hour flow proportioned composite
	INF-01
	See Cond.I.B.3

	Solids, Total  Suspended
	MG/L
	Maximum
	-
	Report
	-
	-
	Weekly
	24-hour flow proportioned composite
	INF-01
	See Cond.I.B.3

	Rainfall
	Inches
	Maximum
	-
	Report (Mo.Total)
	-
	-
	Monthly
	Calculation
	OTH-01
	


2. Samples shall be taken at the monitoring site locations listed in Permit Condition I.B.1 and as described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	FLW-01
	Flow as measured at the headworks prior to treatment and ahead of the return activated sludge line

	INF-01
	at headworks, prior to treatment and ahead of the return activated sludge line.

	OTH-01
	Rain Gauge.


3. Influent samples shall be collected so that they do not contain digester supernatant, return activated sludge, or any other plant process recycled waters. [62-601.500(4)]
4. Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  

5. Parameters which must be monitored as a result of a surface water discharge shall be analyzed using a sufficiently sensitive method to assure compliance with applicable water quality standards and effluent limitations in accordance with 40 CFR (Code of Federal Regulations) Part 136.  Parameters which must be as a result of a ground water discharge (i.e. , underground injection or land application system) shall be analyzed in accordance with Chapter 62-601, F.A.C.  All monitoring shall be representative of the monitored activity. [62-620.320(6)]
6. The permittee shall provide safe access points for obtaining representative influent, reclaimed water, and effluent samples which are required by this permit. [62-601.500(5)]
7. Monitoring requirements under this permit are effective on the first day of the second month following permit issuance.  Until such time, the permittee shall continue to monitor and report in accordance with previously effective permit requirements, if any.  During the period of operation authorized by this permit, the permittee shall complete and submit to the Department Discharge Monitoring Reports (DMRs) in accordance with the frequencies specified by the REPORT type (i.e., monthly, toxicity, quarterly, semiannual, annual, etc.) indicated on the DMR forms attached to this permit.  Monitoring results for each monitoring period shall be submitted in accordance with the associated DMR due dates below, unless specified otherwise in the permit.
	REPORT Type
	Monitoring Period
	Due Date

	Monthly or Toxicity
	first day of month – last day of month
	28th day of following month

	Quarterly
	January 1 - March 31
April 1 – June 30
July 1 – September 30 
October 1 – December 31 
	April 28
July 28
October 28
January 28

	Semiannual
	January 1 – June 30
July 1 – December 31 
	July 28
January 28

	Annual
	January 1 – December 31
	January 28 


DMRs shall be submitted for each required monitoring period including months of no discharge.  The permittee shall make copies of the attached DMR forms and shall submit the completed DMR forms to the Department by the 28th of the month following the month of operation at the address specified below: 

Originals to:

Florida Department of Environmental Protection

Wastewater Compliance Evaluation Section, Mail Station 3551

Bob Martinez Center

2600 Blair Stone Road

Tallahassee, Florida  32399-2400

Copies to:

Florida Department of Environmental Protection

Domestic Wastewater Program

Southwest District Office

13051 N. Telecom Parkway

Temple Terrace, Florida 33637-0926

 [62-620.610(18)][62-601.300(1),(2), and (3)]
8. During the period of operation authorized by this permit, reclaimed water or effluent shall be monitored annually for the primary and secondary drinking water standards contained in Chapter 62-550, F.A.C., (except for asbestos, color, and corrosivity).  Twenty-four hour composite samples or grab samples where appropriate shall be used to analyze reclaimed water or effluent for the primary and secondary drinking water standards.  These monitoring results shall be reported to the Department annually on the DMR under monitoring group number RWS-01.  During years when a permit is not renewed, a certification stating that no new non-domestic wastewater dischargers have been added to the collection system since the last reclaimed water or effluent analysis was conducted may be submitted in lieu of the report.  The annual reclaimed water or effluent analysis report or the certification shall be completed and submitted in a timely manner so as to be received by the Department’s Southwest District Office by June 28 of each year.  Approved analytical methods identified in Rule 62-620.100(3)(j), F.A.C., shall be used for the analysis.  If no method is included for a parameter, methods specified in Chapter 62-550, F.A.C, shall be used.  [62-601.300(4)][62-601.500(3)] [62-610.300(4)]
9. The permittee shall submit an Annual Reuse Report using DEP Form 62-610.300(4)(a)2. on or before January 1 of each year.  [62-610.870(3)]
10. The permittee shall maintain an inventory of storage systems.  The inventory shall be submitted to the Department at least 30 days before reclaimed water will be introduced into any new storage system.  The inventory of storage systems shall be attached to the annual submittal of the Annual Reuse Report.  [62-610.464(5)]
11. Unless specified otherwise in this permit, all reports and other information required by this permit, including 24-hour notifications, shall be submitted to or reported to, as appropriate, the Department's Southwest District Office at the address specified below:

Southwest District Office

13051 N. Telecom Parkway
Temple Terrace, Florida  33637-0926

Phone Number - 813-632-7600

FAX Number -  813-632-7662

All FAX copies shall be followed by original copies.  All reports and other information shall be signed in accordance with the requirements of Rule 62-620.305, F.A.C.   [62-620.305]
II.
RESIDUALS MANAGEMENT REQUIREMENTS 

1.  The method of residuals use or disposal by this facility is transport to South Cross Bayou WRF (FL0040436) or disposal in a Class I solid waste landfill.  Transportation of the residuals to an alternative RMF does not require a permit modification, however, use of an alternative RMF requires a copy of the agreement pursuant to Chapter 62-640.880(1)(c) along with a written notification to the Department at least 30 days before transport of the residuals.
2.  The permittee shall be responsible for proper treatment, management, use, and land application or disposal of its residuals.  [62-640.300(5)]
3. The permittee shall not be held responsible for treatment, management, use, or land application violations that occur after its residuals have been accepted by a permitted residuals management facility with which the source facility has an agreement in accordance with Rule 62-640.880(1)(c), F.A.C., for further treatment, management, use or land application.  [62-640.300(5)]
4. Disposal of residuals, septage, and other solids in a solid waste landfill, or disposal by placement on land for purposes other than soil conditioning or fertilization, such as at a monofill, surface impoundment, waste pile, or dedicated site, shall be in accordance with Chapter 62-701, F.A.C.  [62-640.100(6)(k)3 & 4]  

5. If the permittee intends to accept residuals from other facilities, a permit revision is required pursuant to Rule 62-640.880(2)(d), F.A.C. [62-640.880(2)(d)]  

6. The permittee shall keep hauling records to track the transport of residuals between facilities.  The hauling records shall contain the following information:  

	Source Facility
	Residuals Management Facility or Treatment Facility

	1.
Date and Time Shipped
	1.
Date and Time Received

	2.
Amount of Residuals Shipped
	2.
Amount of Residuals Received

	3.
Degree of Treatment (if applicable)
	3.
Name and ID Number of Source Facility

	4.
Name and ID Number of Residuals 
	4.
Signature of Hauler

	
Management Facility or Treatment Facility
	5.
Signature of Responsible Party at Residuals Management Facility or Treatment Facility

	5. 
Signature of Responsible Party at Source Facility
	

	6. 
Signature of Hauler and Name of Hauling Firm
	


These records shall be kept for five years and shall be made available for inspection upon request by the Department.  A copy of the hauling records information maintained by the source facility shall be provided upon delivery of the residuals to the residuals management facility or treatment facility.  The permittee shall report to the Department within 24 hours of discovery any discrepancy in the quantity of residuals leaving the source facility and arriving at the residuals management facility or treatment facility.  [62-640.880(4)]  ]  

III.
GROUND WATER REQUIREMENTS

Operational Requirements

1. For the Part III Public Access system, all ground water quality criteria specified in Chapter 62-520, F.A.C., shall be met at the edge of the zone of discharge.  The zone of discharge shall extend horizontally 100 feet from the application site or to user’s site property line, whichever is less, and vertically to the base of the surficial aquifer. [62-520.200(27)]  [62-520.465]
2. The ground water minimum criteria specified in Rule 62-520.400 F.A.C., shall be met within the zone of discharge.  [62-520.400 and 62-520.420(4)]
3. During the period of operation authorized by this permit, the permittee shall sample ground water in accordance with this permit and the approved ground water monitoring plan prepared in accordance with Rule 62-520.600, F.A.C.  [62-520.600][62-610.463(3)]
4. The following monitoring wells shall be sampled in accordance with the monitoring frequencies specified in Permit Condition III.5 for Reuse System R-001.  Quarterly sampling must be reasonably spaced to be representative of potentially changing conditions.

	Monitoring Well ID
	Alternate Well Name and/or Description of Monitoring Location
	Depth

(Feet)
	Aquifer Monitored
	New or

Existing

	MWB-01
	NP104 at Wm. Dunn WRF
	31.75
	Surficial
	existing

	MWB-02
	NS07 at West GSA
	24.32
	Surficial
	existing

	MWB-03
	NS06 at West GSA
	68.00
	Floridan
	existing

	MWB-04
	PR103 at Pine Ridge
	20.74
	Surficial
	existing

	MWI-01
	NP156A at Wm. Dunn WRF
	23.65
	Surficial
	existing

	MWC-01
	NP128 at Wm. Dunn WRF
	40.71
	Floridan
	existing

	MWC-03
	NP101A at Wm. Dunn WRF
	49.40
	Surficial
	existing

	MWC-04
	NP143 at Wm. Dunn WRF
	20.50
	Surficial
	existing

	MWC-05
	NP103B at Wm. Dunn WRF
	32.01
	Surficial
	existing

	MWC-06
	NP105A at Wm. Dunn WRF
	21.77
	Surficial
	existing

	MWC-07
	 CR103 at Crescent Oaks
	24.44
	Surficial
	existing

	MWC-08
	WW106 at Wentworth GC
	30.60
	Surficial
	existing

	MWC-09
	TLV178 at Tarpon Lake Village
	21.65
	Surficial
	existing

	MWC-10
	ELW115 at East Lake Woodlands
	20.00
	Surficial
	existing

	MWC-11
	NP182 at Wm. Dunn WRF
	40.00
	Surficial
	existing


MWB = Background;  MWI = Intermediate;  MWC = Compliance
[62-520.600][62-610.463]   
5. The following parameters shall be analyzed for each of the monitoring wells identified in Permit Condition III.4:

	Parameter
	Compliance Well Limit
	Units
	Sample Type
	Monitoring Frequency

	Water Level Relative to NGVD
	Report
	FEET
	In-situ
	Quarterly

	Nitrogen, Nitrate, Total (as N)
	10
	MG/L
	Grab
	Quarterly

	Solids, Total Dissolved (TDS)
	500
	MG/L
	Grab
	Quarterly

	Arsenic, Total Recoverable
	10
	UG/L
	Grab
	Quarterly

	Chloride (as Cl)
	250
	MG/L
	Grab
	Quarterly

	Cadmium, Total Recoverable
	5
	UG/L
	Grab
	Quarterly

	Chromium, Total Recoverable
	100
	UG/L
	Grab
	Quarterly

	Lead, Total Recoverable
	15
	UG/L
	Grab
	Quarterly

	Coliform, Fecal
	4
	#/100ML
	Grab
	Quarterly

	pH*
	6.5 to 8.5
	SU
	In-situ
	Quarterly

	Sulfate, Total
	250
	MG/L
	Grab
	Quarterly

	Turbidity*
	Report
	NTU
	In-situ
	Quarterly

	Temperature (C), Water*
	Report
	DEG.C
	In-situ
	Quarterly

	Specific Conductance*
	Report
	UMHO/CM
	In-situ
	Quarterly

	Sodium, Total Recoverable
	160
	MG/L
	Grab
	Quarterly

	Oxygen, Dissolved  (DO)*
	Report
	MG/L
	In-situ
	Quarterly


*The field parameters shall be sampled per DEP–SOP-001/01, FS 2200 Groundwater Sampling and recorded, (see Figure FS 2200-2 Groundwater Purging Procedure and Form FD 9000-24, Groundwater Sampling Log). The field parameters to be reported on Part D of GW DMR shall be the last sample recorded.
[62-520.600(11)(b)] [62-601.300(3), 62-601.700, and Figure 3 of 62-601][62-601.300(6)] [62-520.300(9)]
6. If the concentration for any constituent listed in Permit Condition III.5 in the natural background quality of the ground water is greater than the stated maximum, or in the case of pH is also less than the minimum, the representative natural background quality shall be the prevailing standard.  [62-520.420(2)]  

7. In accordance with Part D of Form 62-620.910(10), water levels shall be recorded before evacuating wells for sample collection.  Elevation references shall include the top of the well casing and land surface at each well site (NGVD allowable) at a precision of plus or minus 0.1 foot.  [62-520.600(11)(c) ]  

8. Ground water monitoring wells shall be purged prior to sampling to obtain representative samples.  [62-601.700(5)]  

9. Analyses shall be conducted on unfiltered samples, unless filtered samples have been approved by the Department's Southwest District Office as being more representative of ground water conditions.  [62-520.310(5)]  

10. Ground water monitoring parameters shall be analyzed in accordance with Chapter 62-601, F.A.C.  [62-610.320(3) and 62-620.610(18)] 

11. For permit renewal, the permittee shall submit, to the Southwest District Office, the results of sampling monitoring wells specified in the Department-approved monitoring plan for the primary and secondary drinking water parameters included in Chapter 62-550, F.A.C., (excluding asbestos, acrylamide, Dioxin, butachlor, epichlorohydrin, pesticides, and PCBs, unless reasonably expected to be a constituent of the discharge or an artifact of the site).  Additional volatile and semivolatile parameters as specified in the ground water monitoring plan or permit shall be analyzed.  Sampling shall occur no sooner than 180 days before submittal of the renewal application (The Department-approved groundwater monitoring plan shall be revised as necessary to specify the monitoring wells selected to be sampled at the time of permit renewal).  [62-520.600(5)(b)]
12. Ground water monitoring test results shall be submitted on Part D of Form 62-620.910(10).  For reuse or land application projects, results shall be submitted with the DMR for each month listed in the following schedule.  The submitted results shall be for each year during the period of operation allowed by this permit in accordance with Permit Condition I.C.8.  [62-520.600(11)(b)]  [62-601.300(3), 62.601.700, and Figure 3 of 62-601] [62-620.610(18)]  

	SAMPLE PERIOD
	REPORT DUE DATE

	January - March
	April 28

	April - June
	July 28

	July - September
	October 28

	October - December
	January 28


13. If any monitoring well becomes inoperable or damaged to the extent that sampling or well integrity may be affected, the permittee shall notify the Department's Southwest District Office within two business days from discovery, and a detailed written report shall follow within ten days after notification to the Department.  The written report shall detail what problem has occurred and remedial measures that have been taken to prevent recurrence or request approval for replacement of the monitoring well.  All monitoring well design and replacement shall be approved by the Department before installation. [62-520.600(6)(l)] 

14. All piezometers and wells that are not reasonably expected to be used are to be plugged and abandoned in accordance with subsection 62-532.500(4), F.A.C.  The permittee shall submit a written report to the Department’s office that issued the permit providing verification of the plugging including the well abandonment log when available; [62-520.600(6)(k)] 
IV.
ADDITIONAL REUSE AND LAND APPLICATION REQUIREMENTS

Part III Public Access System (R-001)

1. Use of reclaimed water is authorized within the general service area identified in the attached map.  The following uses of reclaimed water are authorized within this general service area:  Athletic Complexes and Parks, Business, Commercial and Industrial Parks, Golf Courses, Residential Developments, Dust Control, Pesticide Mixing, Cooling Towers and Tanker RCW Filling Station at the WWTF.  [62-620.630(10)(d)]
2. This reuse system includes the following major users (i.e., using 0.1 MGD or more of reclaimed water):

	User Name
	User Type
	Capacity

(MGD)
	Acreage

	PCU Landsbrook, East Lake Rd
	Residential Developments
	0.102
	

	Severs Landing
	Residential Developments
	0.11
	32.5

	Innisbrook
	Golf Courses
	1.77
	506

	Wentworth Golf
	Golf Courses
	0.28
	79

	Highland Lakes
	Golf Courses
	0.26
	74

	East Lake Woodlands
	Golf Courses
	0.88
	251

	Tarponwoods
	Golf Courses
	0.41
	118

	Highlands of Innisbrook
	Golf Courses
	0.17
	49

	Pipers Meadow
	Residential Developments
	0.16
	46.2

	Orange Point
	Residential Developments
	0.21
	60.3

	Totals
	4.352
	1216


[62-610.800(5)][62-620.630(10)(b)]
3. New major users of reclaimed water (i.e., using 0.1 MGD or more) may be added to the reuse system using the general permit described in Rule 62-610.890, F.A.C., if the requirements in this rule are complied with.  Application for use of this general permit shall be made using Form 62-610.300(4)(a)1.  [62-610.890]
4. Cross-connections to the potable water system are prohibited.  [62-610.469(7)]
5. A cross-connection control program shall be implemented and/or remain in effect within the areas where reclaimed water will be provided for use.  [62-610.469(7)]
6. The permittee shall conduct inspections within the reclaimed water service area to verify proper connections, to minimize illegal cross-connections, and to verify the proper use of reclaimed water.  Inspections are required when a customer first connects to the reuse distribution system.  Subsequent inspections are required as specified in the cross-connection control and inspection program.  [62-610.469(7)(h)]
7. If a cross-connection between the potable and reclaimed water systems is discovered, the permittee shall:

a.
Immediately discontinue potable water and/or reclaimed water service to the affected area.

b.
If the potable water system is contaminated, clear the potable water lines.

c.
Eliminate the cross-connection.

d.
Test the affected area for other possible cross-connections.

e.
Within 24 hours, notify the Southwest District Office's domestic wastewater and drinking water programs, and the Pinellas County Health Department's drinking water program.

f.
Within 5 days of discovery of a cross-connection, submit a written report to the Department detailing: a description of the cross-connection, how the cross-connection was discovered, the exact date and time of discovery, approximate time that the cross-connection existed, the location, the cause, steps taken to eliminate the cross-connection, whether reclaimed water was consumed, and reports of possible illness, whether the drinking water system was contaminated and the steps taken to clear the drinking water system, when the cross-connection was eliminated, plan of action for testing for other possible cross-connections in the area, and an evaluation of the cross-connection control and inspection program to ensure that future cross-connections do not occur.  [62-555.350(3) and 62-555.360][62-620.610(20)]
8. Maximum obtainable separation of reclaimed water lines and potable water lines shall be provided and the minimum separation distances specified in Rule 62-610.469(7), F.A.C., shall be provided.  Reuse facilities shall be color coded or marked.  Underground piping which is not manufactured of metal or concrete shall be color coded using Pantone Purple 522C using light stable colorants.  Underground metal and concrete pipe shall be color coded or marked using purple as the predominant color.  [62-610.469(7)]
9. In constructing reclaimed water distribution piping, the permittee shall maintain a 75-foot setback distance from a reclaimed water transmission facility to public water supply wells.  No setback distances are required to other potable water supply wells or to any nonpotable water supply wells.  [62-610.471(3)]
10. A setback distance of 75 feet shall be maintained between the edge of the wetted area and potable water supply wells, unless the utility adopts and enforces an ordinance prohibiting potable water supply wells within the reuse service area.  No setback distances are required to any nonpotable water supply well, to any surface water, to any developed areas, or to any private swimming pools, hot tubs, spas, saunas, picnic tables, barbecue pits, or barbecue grills.  [62-610.471(1), (2), (5), and (7)]
11. Reclaimed water shall not be used to fill swimming pools, hot tubs, or wading pools.  [62-610.469(4)]
12. Low trajectory nozzles, or other means to minimize aerosol formation shall be used within 100 feet from outdoor public eating, drinking, or bathing facilities.  [62-610.471(6)]
13. A setback distance of 100 feet shall be maintained from indoor aesthetic features using reclaimed water to adjacent indoor public eating and drinking facilities.  [62-610.471(8)]
14. The public shall be notified of the use of reclaimed water.  This shall be accomplished by posting of advisory signs in areas where reuse is practiced, notes on scorecards, or other methods.  [62-610.468(2)]
15. All new advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets shall bear the words “do not drink” and “no beber” along with the equivalent standard international symbol.  In addition to the words “do not drink” and “no beber,” advisory signs posted at storage ponds and decorative water features shall also bear the words “do not swim” and “no nadar” along with the equivalent standard international symbols.  Existing advisory signs and labels shall be retrofitted, modified, or replaced in order to comply with the revised wording requirements.  For existing advisory signs and labels this retrofit, modification, or replacement shall occur within 365 days after the date of this permit.  For labels on existing vaults, service boxes, or compartments housing hose bibbs this retrofit, modification, or replacement shall occur within 730 days after the date of this permit.  [62-610.468 & 62-610.469]
16. The permittee shall ensure that users of reclaimed water are informed about the origin, nature, and characteristics of reclaimed water; the manner in which reclaimed water can be safely used; and limitations on the use of reclaimed water. Notification is required at the time of initial connection to the reclaimed water distribution system and annually after the reuse system is placed into operation.  A description of on-going public notification activities shall be included in the Annual Reuse Report.  [62-610.468(6)]
17. Routine aquatic weed control and regular maintenance of storage pond embankments and access areas are required.  [62-610.414 & 62-610.464]
18. Overflows from emergency discharge facilities on storage ponds shall be reported as an abnormal event to the Department's Southwest District Office within 24 hours of an occurrence.  The provisions of Rule 62-610.800(9), F.A.C., shall be met.  [62-610.800(9)]
Supplemental ASR 
Aquifer Storage and Recovery (ASR)

19. All applications for permit renewals shall include an evaluation of the performance of the ASR system. This shall include evaluations of monitoring data (including trends observed), any problems encountered, and any anticipated problems based on review of the monitoring trends. Existing and anticipated problems shall be addressed as described in Permit Condition IV.20.  [62-610.466(6)]
20. The permittee shall assess the performance of the aquifer storage and recovery system on a monthly basis.  During operation of the reuse system, if it is shown that water recovered from the aquifer storage and recovery system does not meet the fecal coliform performance criteria associated with high-level disinfection or if the water recovered adversely affects vegetation or crops grown in the reuse system or adversely affects the infiltration/percolation capability of soils within the reuse system, the permittee shall do the following:

a. 
Evaluate the nature and severity of the problems.

b. 
Propose remedial or preventative measures and provide reasonable assurances that the remedial or preventative measures will avoid future occurrences of the adverse effects. Remedial or preventative measures may include additional monitoring of or additional treatment of the water recovered from the aquifer storage and recovery system, or other measures.

c. 
Propose a time schedule for implementation of the proposed remedial or preventative measures.

d. 
Submit a written report to the Department within 120 days of identification of a potential problem. The report shall address the requirements of Items a through c, above. [62-610.466(17)]

Supplemental Water Supplies – Lake Tarpon 
21.
The mixture of reclaimed water and Lake Tarpon shall not harm vegetation or crops grown in the reuse system. [62-610.472(3)]

22.
A one-way flow device shall be provided on each Lake Tarpon’s supply line to prevent backflow of reclaimed water into the surface water, the ASR well or stormwater treatment facilities. [62-610.472(3)]

23.
The supplemental water supply pipes and appurtenances shall be color coded and marked to differentiate them from the reclaimed water and potable water facilities. [62-610.472(3)]
24.
Facilities used to connect supplemental water supplies into the reclaimed water distribution system shall be located and documented in the record drawings for the reuse system. [62-610.472(7)]
V.
OPERATION AND MAINTENANCE REQUIREMENTS

1.
During the period of operation authorized by this permit, the wastewater facilities shall be operated under the supervision of an operator certified in accordance with Chapter 62-602, F.A.C.  In accordance with Chapter 62-699, F.A.C., this facility is a Category I, Class A facility and, at a minimum, operators with appropriate certification must be on the site as follows:

A Class C or higher operator 24 hours/day for 7 days/week.  The lead operator must be a Class A.

[62-620.630(3)] [62-699.310] [62-610.462]
2. The lead operator shall be employed at the plant full time.  “Full time” shall mean at least four days per week, working a minimum of 35 hours per week, including leave time.  A certified operator shall be on-site and in charge of each required shift and for periods of required staffing time when the lead operator is not on-site.  An operator meeting the lead operator classification level of the plant shall be available during all periods of plant operation.  “Available” means able to be contacted as needed to initiate the appropriate action in a timely manner.  [62-699.311(10), (5) and (1)]
3. The application to renew this permit shall include an updated capacity analysis report prepared in accordance with Rule 62-600.405, F.A.C.  [62-600.405(5)]
4. The application to renew this permit shall include a detailed operation and maintenance performance report prepared in accordance with Rule 62-600.735, F.A.C.  [62-600.735(1)]
5. The permittee shall maintain the following records and make them available for inspection  on the site of the permitted facility:

a.
Records of all compliance monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation and a copy of the laboratory certification showing the certification number of the laboratory, for at least three years from the date the sample or measurement was taken;

b.
Copies of all reports required by the permit for at least three years from the date the report was prepared;

c.
Records of all data, including reports and documents, used to complete the application for the permit for at least three years from the date the application was filed;

d.
Monitoring information, including a copy of the laboratory certification showing the laboratory certification number, related to the residuals use and disposal activities for the time period set forth in Chapter 62-640, F.A.C., for at least three years from the date of sampling or measurement;

e.
A copy of the current permit;

f.
A copy of the current operation and maintenance manual as required by Chapter 62-600,. F.A.C.;

g.
A copy of the facility record drawings;

h.
Copies of the licenses of the current certified operators; and 

i.
Copies of the logs and schedules showing plant operations and equipment maintenance for three years from the date of the logs or schedules.  The logs shall, at a minimum, include identification of the plant; the signature and certification number of the operator(s) and the signature of the person(s) making any entries; date and time in and out; specific operation and maintenance activities; tests performed and samples taken; and major repairs made. The logs shall be maintained on-site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed.


[62-620.350]
VI.
SCHEDULES

1. The following construction schedule for the facilities shall be followed, unless a minor permit revision is issued to amend the schedule:

	Implementation Step
	Completion Date

	1
	Submit to the Department the results of the pilot testing program, including addressing the items in Rule 62-610.472(3) for Department review and approval.
	Prior to placing the supplemental water system into service.

	2
	Provide appropriate documentation as required in permit conditions VIII. 1 & 2 for placing any new facilities or unit processes into operation.


	As required by permit conditions VIII. 1 & 2 




[62-620.400]
VII.  INDUSTRIAL PRETREATMENT PROGRAM REQUIREMENTS

1. The permittee shall function as the Control Authority and shall be responsible for the performance of all pretreatment program requirements contained in Chapter 62-625, F.A.C.  The permittee shall be subject to enforcement actions, penalties, and other remedies by the Department or other appropriate parties.  The permittee shall implement and enforce its Approved Pretreatment Program.  The permittee's Approved Pretreatment Program is hereby made an enforceable condition of this permit.  The Department may initiate enforcement action against an industrial user for noncompliance with applicable standards and requirements. [62-625.500]
2. The permittee shall enforce the requirements promulgated under Sections 307(b), 307(c), 307(d), and 402(b) of the Act.  The permittee shall cause industrial users subject to Federal Categorical Standards to achieve compliance no later than the date specified in those requirements or, in the case of new industrial users, upon commencement of the discharge. [62-625.410]
3. The permittee shall perform the pretreatment functions as required in Chapter 62-625, F.A.C., including, but not limited to, the following:

a.
Implementing the necessary legal authorities as provided in Rule 62-625.500(2)(a), F.A.C.  This includes, among other things, the authority to require compliance with applicable pretreatment standards, which includes general prohibitions listed in Rule 62-625.400(1), F.A.C., specific prohibitions in Rule 62-625.400(2), F.A.C., locally developed limits as required by Rules 62-625.400(3) and (4), F.A.C., and national categorical limits in accordance with Rule 62-625.410, F.A.C.; 

b.
Implementing the programmatic functions as required under Rule 62-625.500(2)(b), F.A.C.; 

c.
Providing the required funding, equipment, and personnel to implement the pretreatment program as provided in Rules 62-625.500(2), (3), and (4), F.A.C.; and

d.
Providing a written technical evaluation that local limits have been developed in accordance with Rule 62-625.400(3)(a), F.A.C.  The evaluation shall verify whether existing local limits protect the wastewater facilities, and if not, the permittee shall develop new local limits as part of the evaluation.  The permittee shall continue to develop these limits as necessary and effectively enforce such limits.

 [62-625.400 and .500]
4. As required by Rules 62-625.600(8) and (12), F.A.C., the permittee shall submit a signed copy of the annual report for pretreatment activities, including DMRs for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R, to the Department at the following address:

Florida Department of Environmental Protection

Domestic Wastewater Section, Mail Station 3540

Bob Martinez Center
2600 Blair Stone Road

Tallahassee, Florida 32399-2400


The annual report shall contain the information required in accordance with Rule 62‑625.600(8), F.A.C., except section (8)(e) as noted below, and shall describe the permittee's pretreatment activities for the reporting year.  In the event that the permittee is not in compliance with any conditions or requirements of the pretreatment program, then the permittee shall also include the reasons for noncompliance and state how and when the permittee shall comply with such conditions and requirements.  


In order to comply with Rule 62-625.600(8)(e), F.A.C., the permittee shall submit annual DMRs with the analytical results of influent, effluent, and residuals for those pollutants listed on the DMRs.  For any other nonpriority pollutants which the permittee believes may be causing or contributing to interference, pass through, or adversely impacting residuals quality, the annual report shall provide a summary of all analytical results of influent, effluent, and residuals.  The annual report and DMRs are due on May 1 of each year.


[62-625.600(12)]
5. Samples for Monitoring Group Numbers PRT-I, PRT-E, and PRT-R shall be taken at the monitoring site locations described below:

	Monitoring Location Site Number
	Description of Monitoring Location

	PRT-I
	At headworks, prior to treatment and ahead of the return activated sludge line.

	PRT-E
	After disinfection and prior to the public access reuse system (R-001).

	PRT-R
	Discharge at dewatering press.


VIII.  OTHER SPECIFIC CONDITIONS

1. Prior to placing the modified portions of the existing facilities into operation or any individual unit processes into operation, for any purpose other than testing for leaks and equipment operation, the permittee shall complete and submit to the Department DEP Form 62-620.910(12), Notification of Completion of Construction for Domestic Wastewater Facilities.  [62-620.630(2)] 
2. Within six months after a facility is placed in operation, the permittee shall provide written certification to the Department on Form 62-620.910(13) that record drawings pursuant to Chapter 62-600, F.A.C., and that an operation and maintenance manual pursuant to Chapters 62-600 and 62-610, F.A.C., as applicable, are available at the location specified on the form.  [62-620.630(7)]
3. The permittee shall apply for renewal of this permit at least 180 days before the expiration date of the permit using the appropriate forms listed in Rule 62-620.910, F.A.C., including submittal of the appropriate processing fee set forth in Rule 62-4.050, F.A.C.  The existing permit shall not expire until the Department has taken final action on the application renewal in accordance with the provisions of 62-620.335(3) and (4), F.A.C.  [62-620.335(1)-(4)]
4. Florida water quality criteria and standards shall not be violated as a result of any discharge or land application of reclaimed water or residuals from this facility.  [62-620.320(9) and 62-302.500(2)(e)][62-610.850(1)(a) and (2)(a)]
5. In the event that the treatment facilities or equipment no longer function as intended, are no longer safe in terms of public health and safety, or odor, noise, aerosol drift, or lighting adversely affects neighboring developed areas at the levels prohibited by Rule 62-600.400(2)(a), F.A.C., corrective action (which may include additional maintenance or modifications of the permitted facilities) shall be taken by the permittee.  Other corrective action may be required to ensure compliance with rules of the Department.  Additionally, the treatment, management, use or land application of residuals shall not cause a violation of the odor prohibition in Rule 62-296.320(2), F.A.C.  [62-600.410(8) and 62-640.400(6)]
6. The deliberate introduction of stormwater in any amount into collection/transmission systems designed solely for the introduction (and conveyance) of domestic/industrial wastewater; or the deliberate introduction of stormwater into collection/transmission systems designed for the introduction or conveyance of combinations of storm and domestic/industrial wastewater in amounts which may reduce the efficiency of pollutant removal by the treatment plant is prohibited, except as provided by Rule 62-610.472, F.A.C.  [62-604.130(3)]
7. Collection/transmission system overflows shall be reported to the Department in accordance with Permit Condition IX. 20.  [62-604.550]  [62-620.610(20)]
8. The operating authority of a collection/transmission system and the permittee of a treatment plant are prohibited from accepting connections of wastewater discharges which have not received necessary pretreatment or which contain materials or pollutants (other than normal domestic wastewater constituents):

a.
Which may cause fire or explosion hazards; or

b.
Which may cause excessive corrosion or other deterioration of wastewater facilities due to chemical action or pH levels; or

c.
Which are solid or viscous and obstruct flow or otherwise interfere with wastewater facility operations or treatment; or

d.
Which result in the wastewater temperature at the introduction of the treatment plant exceeding 40oC or otherwise inhibiting treatment; or

e.
Which result in the presence of toxic gases, vapors, or fumes that may cause worker health or safety problems.

[62-604.130(5)]
9. The treatment facility, storage ponds, rapid infiltration basins, and/or infiltration trenches shall be enclosed with a fence or otherwise provided with features to discourage the entry of animals and unauthorized persons.  [62-600.400(2)(b)]
10. Screenings and grit removed from the wastewater facilities shall be collected in suitable containers and hauled to a Department approved Class I landfill or to a landfill approved by the Department for receipt/disposal of screenings and grit.  [62-701.300(1)(a)]
11. The permittee shall provide verbal notice to the Department as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department in a written report within seven days of the sinkhole discovery.  [62-4.070(3)]
IX.
GENERAL CONDITIONS

1.
The terms, conditions, requirements, limitations and restrictions set forth in this permit are binding and enforceable pursuant to Chapter 403, Florida Statutes.  Any permit noncompliance constitutes a violation of Chapter 403, Florida Statutes, and is grounds for enforcement action, permit termination, permit revocation and reissuance, or permit revision.  [62-620.610(1)]

2.
This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviations from the approved drawings, exhibits, specifications or conditions of this permit constitutes grounds for revocation and enforcement action by the Department.  [62-620.610(2)]
3.
As provided in subsection 403.087(7), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor authorize any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit or authorization that may be required for other aspects of the total project which are not addressed in this permit.  [62-620.610(3)]
4.
This permit conveys no title to land or water, does not constitute state recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [62-620.610(4)]

5.
This permit does not relieve the permittee from liability and penalties for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source; nor does it allow the permittee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department.  The permittee shall take all reasonable steps to minimize or prevent any discharge, reuse of reclaimed water, or residuals use or disposal in violation of this permit which has a reasonable likelihood of adversely affecting human health or the environment.  It shall not be a defense for a permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this permit.  [62-620.610(5)]
6.
If the permittee wishes to continue an activity regulated by this permit after its expiration date, the permittee shall apply for and obtain a new permit.  [62-620.610(6)]
7.
The permittee shall at all times properly operate and maintain the facility and systems of treatment and control, and related appurtenances, that are installed and used by the permittee to achieve compliance with the conditions of this permit.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to maintain or achieve compliance with the conditions of the permit.  [62-620.610(7)]

8.
This permit may be modified, revoked and reissued, or terminated for cause.  The filing of a request by the permittee for a permit revision, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition.  [62-620.610(8)]

9.
The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, including an authorized representative of the Department and authorized EPA personnel, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated, to:

a.
Enter upon the permittee’s premises where a regulated facility, system, or activity is located or conducted, or where records shall be kept under the conditions of this permit;

b.
Have access to and copy any records that shall be kept under the conditions of this permit;

c.
Inspect the facilities, equipment, practices, or operations regulated or required under this permit; and

d.
Sample or monitor any substances or parameters at any location necessary to assure compliance with this permit or Department rules.


[62-620.610(9)]

10.
In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data, and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except as such use is proscribed by Section 403.111, Florida Statutes, or Rule 62-620.302, Florida Administrative Code.  Such evidence shall only be used to the extent that it is consistent with the Florida Rules of Civil Procedure and applicable evidentiary rules.  [62-620.610(10)]

11.
When requested by the Department, the permittee shall within a reasonable time provide any information required by law which is needed to determine whether there is cause for revising, revoking and reissuing, or terminating this permit, or to determine compliance with the permit.  The permittee shall also provide to the Department upon request copies of records required by this permit to be kept.  If the permittee becomes aware of relevant facts that were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be promptly submitted or corrections promptly reported to the Department.  [62-620.610(11)]

12.
Unless specifically stated otherwise in Department rules, the permittee, in accepting this permit, agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.  A reasonable time for compliance with a new or amended surface water quality standard, other than those standards addressed in Rule 62-302.500, F.A.C., shall include a reasonable time to obtain or be denied a mixing zone for the new or amended standard.  [62-620.610(12)]

13.
The permittee, in accepting this permit, agrees to pay the applicable regulatory program and surveillance fee in accordance with Rule 62-4.052, F.A.C.  [62-620.610(13)]

14.
This permit is transferable only upon Department approval in accordance with Rule 62-620.340, F.A.C.  The permittee shall be liable for any noncompliance of the permitted activity until the transfer is approved by the Department.  [62-620.610(14)]

15.
The permittee shall give the Department written notice at least 60 days before inactivation or abandonment of a wastewater facility and shall specify what steps will be taken to safeguard public health and safety during and following inactivation or abandonment.  [62-620.610(15)]

16.
The permittee shall apply for a revision to the Department permit in accordance with Rules 62-620.300 and the Department of Environmental Protection Guide to Wastewater Permitting at least 90 days before construction of any planned substantial modifications to the permitted facility is to commence or with Rule 62-620.325(2) for minor modifications to the permitted facility.  A revised permit shall be obtained before construction begins except as provided in Rule 62-620.300, F.A.C.  [62-620.610(16)]
17.
The permittee shall give advance notice to the Department of any planned changes in the permitted facility or activity which may result in noncompliance with permit requirements.  The permittee shall be responsible for any and all damages which may result from the changes and may be subject to enforcement action by the Department for penalties or revocation of this permit.  The notice shall include the following information:

a.
A description of the anticipated noncompliance;

b.
The period of the anticipated noncompliance, including dates and times; and

c.
Steps being taken to prevent future occurrence of the noncompliance.


[62-620.610(17)]

18.
Sampling and monitoring data shall be collected and analyzed in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.

a.
Monitoring results shall be reported at the intervals specified elsewhere in this permit and shall be reported on a Discharge Monitoring Report (DMR), DEP Form 62-620.910(10), or as specified elsewhere in the permit.

b.
If the permittee monitors any contaminant more frequently than required by the permit, using Department approved test procedures, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the DMR.

c.
Calculations for all limitations which require averaging of measurements shall use an arithmetic mean unless otherwise specified in this permit.

d.
Except as specifically provided in Rule 62-160.300, F.A.C., any laboratory test required by this permit shall be performed by a laboratory that has been certified by the Department of Health Environmental Laboratory Certification Program (DOH ELCP).  Such certification shall be for the matrix, test method and analyte(s) being measured to comply with this permit.  For domestic wastewater facilities, testing for parameters listed in Rule 62-160.300(4), F.A.C., shall be conducted under the direction of a certified operator.

e.
Field activities including on-site tests and sample collection shall follow the applicable standard operating procedures described in DEP-SOP-001/01 adopted by reference in Chapter 62-160, F.A.C.  

f.
Alternate field procedures and laboratory methods may be used where they have been approved in accordance with Rules 62-160.220 and 62-160.330, F.A.C.


[62-620.610(18)]
19.
Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule detailed elsewhere in this permit shall be submitted no later than 14 days following each schedule date.  [62-620.610(19)]

20.
The permittee shall report to the Department any noncompliance which may endanger health or the environment.  Any information shall be provided orally within 24 hours from the time the permittee becomes aware of the circumstances.  A written submission shall also be provided within five days of the time the permittee becomes aware of the circumstances.  The written submission shall contain:  a description of the noncompliance and its cause; the period of noncompliance including exact dates and time, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.

a.
The following shall be included as information which must be reported within 24 hours under this condition:

1.
Any unanticipated bypass which causes any reclaimed water or effluent to exceed any permit limitation or results in an unpermitted discharge,

2.
Any upset which causes any reclaimed water or the effluent to exceed any limitation in the permit,

3.
Violation of a maximum daily discharge limitation for any of the pollutants specifically listed in the permit for such notice, and

4.
Any unauthorized discharge to surface or ground waters.

b.
Oral reports as required by this subsection shall be provided as follows:

1.
For unauthorized releases or spills of treated or untreated wastewater reported pursuant to subparagraph a.4 that are in excess of 1,000 gallons per incident, or where information indicates that public health or the environment will be endangered, oral reports shall be provided to the Department by calling the STATE WARNING POINT TOLL FREE NUMBER (800) 320-0519, as soon as practical, but no later than 24 hours from the time the permittee becomes aware of the discharge. The permittee, to the extent known, shall provide the following information to the State Warning Point:

a) Name, address, and telephone number of person reporting;

b) Name, address, and telephone number of permittee or responsible person for the discharge; 

c) Date and time of the discharge and status of discharge (ongoing or ceased); 

d) Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater);

e) Estimated amount of the discharge;

f) Location or address of the discharge; 

g) Source and cause of the discharge; 

h) Whether the discharge was contained on-site, and cleanup actions taken to date; 

i) Description of area affected by the discharge, including name of water body affected, if any; and  

j) Other persons or agencies contacted.

2.
Oral reports, not otherwise required to be provided pursuant to subparagraph b.1 above,  shall be provided to the Department within 24 hours from the time the permittee becomes aware of the circumstances. 

c.
If the oral report has been received within 24 hours, the noncompliance has been corrected, and the noncompliance did not endanger health or the environment, the Department shall waive the written report.


[62-620.610(20)]

21.
The permittee shall report all instances of noncompliance not reported under Permit Conditions IX. 17., 18. and 19. of this permit at the time monitoring reports are submitted.  This report shall contain the same information required by Permit Condition IX. 20 of this permit.  [62-620.610(21)]

22.
Bypass Provisions.

a.
Bypass is prohibited, and the Department may take enforcement action against a permittee for bypass, unless the permittee affirmatively demonstrates that:

1.
Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage; and 

2.
There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

3.
The permittee submitted notices as required under Permit Condition IX. 22. b. of this permit.

b.
If the permittee knows in advance of the need for a bypass, it shall submit prior notice to the Department, if possible at least 10 days before the date of the bypass.  The permittee shall submit notice of an unanticipated bypass within 24 hours of learning about the bypass as required in Permit Condition IX. 20. of this permit.  A notice shall include a description of the bypass and its cause; the period of the bypass, including exact dates and times; if the bypass has not been corrected, the anticipated time it is expected to continue; and the steps taken or planned to reduce, eliminate, and prevent recurrence of the bypass.

c.
The Department shall approve an anticipated bypass, after considering its adverse effect, if the permittee demonstrates that it will meet the three conditions listed in Permit Condition IX. 22. a. 1. through 3. of this permit.

d.
A permittee may allow any bypass to occur which does not cause reclaimed water or effluent limitations to be exceeded if it is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of Permit Condition IX. 22. a. through c. of this permit.


[62-620.610(22)]

23.
Upset Provisions

a.
A permittee who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed contemporaneous operating logs, or other relevant evidence that:

1.
An upset occurred and that the permittee can identify the cause(s) of the upset;

2.
The permitted facility was at the time being properly operated;

3.
The permittee submitted notice of the upset as required in Permit Condition IX. 20. of this permit; and

4.
The permittee complied with any remedial measures required under Permit Condition IX. 5. of this permit.

b.
In any enforcement proceeding, the burden of proof for establishing the occurrence of an upset rests with the permittee.

c.
Before an enforcement proceeding is instituted, no representation made during the Department review of a claim that noncompliance was caused by an upset is final agency action subject to judicial review.

[62-620.610(23)]
Executed in Hillsborough County, Florida.

STATE OF FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION

____________________________________

Jeffry S. Greenwell, P.E.

Water Facilities Administrator

Southwest District
“More Protection, Less Process”
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