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This permit is issued under the provisions of Chapter 403, Florida Statutes, and applicable rules of the Florida Administrative Code (F.A.C.) and constitutes authorization to discharge to waters of the state under the National Pollutant Discharge Elimination System.  The above named permittee is hereby authorized to operate the facilities shown on the application and other documents attached hereto or on file with the Department and made a part hereof and specifically described as follows:
REUSE:

Land Application R-001:  An existing 11.0 mgd Annual Average Daily Flow (AADF) permitted capacity slow-rate public access system (R-001) consisting of a general service area located in the City of Clearwater as defined by the City of Clearwater Year 2000 Reclaimed Water System Review service area boundary map, dated April 3, 2001, as well as defined in Permit Condition IV. 1.

Land Application:  R002:  Transfer of up to 3.0 mgd AADF Part III Public Access Reclaimed Water to the Pinellas County William E. Dunn WRF Master Urban Reuse System (FL0128775), as specified in the Reclaimed Water Supply Agreement, effective February 17, 2000, between the City of Clearwater and the Pinellas County Government, at a transfer point to be agreed mutually.

Reclaimed water meeting Part III public access standards is provided by three existing, separately permitted, City of Clearwater-operated domestic wastewater treatment facilities, as follows:


Marshall Street AWWTP – FL0021857– up to 10.0 MGD AADF


Northeast AWWTP – FL0128937 – up to 13.5 MGD AADF


East AWWTP – FL0021865 – up to 5.0 MGD AADF

Wet weather and reject disposal is available at each source Advanced Wastewater Treatment Facility by alternative disposal using a permitted NPDES surface water discharge with capacity up to each plant’s ability to generate reclaimed water.

Effluent quality is continuously monitored at the source wastewater treatment facilities for high-level disinfection in accordance with each facility’s approved operating protocol.  For all source facilities, the on-site and off-site storage is controlled, sequenced, and operated during staffed and unstaffed periods according to procedures set forth in an operating protocols established for each source facility in order to assure maximum reliability and safeguards on the quality of the reclaimed water.

The following locations, under the control of the City of Clearwater Utilities, provide storage:

	Storage Basin
	Storage Capacity (MG)
	Type of Storage

	Northeast AWWTF
	6.0
	Two Ground Storage Tanks

	Marshall Street AWWTF
	5.0
	One Ground Storage Tank 


The following locations provide additional storage:

	Storage Basin
	Storage Capacity (MG)
	Type of Storage

	Countryside Country Club
	0.760 to 1.52 
	Unlined Pond

	Chi Chi Rodriguez Golf Course
	0.550 to 1.10
	Unlined Pond

	PGA Driving Range
	1.0
	Unlined Pond

	Clearwater Country Club
	0.690
	Unlined Pond


DISPOSAL:

Intermittently discharging stormwater storage ponds for Part III Reclaimed Water:
Reclaimed water is stored in storm water storage lake system at D-001, Countryside Country Club Pond, which intermittently overflows to; Possum Creek and thence to Tampa Bay.
IN ACCORDANCE WITH: The limitations, monitoring requirements and other conditions set forth in Pages 1 through 21 of this permit

I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.
Reuse and Land Application Systems

1.  During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to direct reclaimed water to Reuse System R-001.  Such reclaimed water shall be limited and monitored by the permittee as specified below:

	Total System
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (Total Flow, City of Clearwater MRS)

To R-001
	MGD
	Maximum
	11.0
	Report
	-
	-
	Monthly
	Calculation
	FLW-01
	See Cond.I.A.4


	Total System Inflows
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (Marshall Street AWWTP)

FL0021857
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-02
	See Cond.I.A.4

	Flow (Northeast AWWTP)

FL0128937
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-03
	See Cond.I.A.4

	Flow (East AWWTP)

FL0021865
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-04
	See Cond.I.A.4


* The permitted Annual Average Daily Flow (AADF) into the City of Clearwater Master Reuse System for each individual source facility is contained in the corresponding treatment facility permit.
	Rain Gauge Monitoring 
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Total
	Monthly

Total
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Rainfall at Marshall Street AWWTP, FL0021857
	Inches
	Maximum
	Report
	Report
	-
	-
	Continuous

(Daily Reading)
	Rain Gauge
	OTH-AWRG
	

	Rainfall at Northeast AWWTP

FL0128937
	Inches
	Maximum
	Report
	Report
	-
	-
	Continuous

(Daily Reading)
	Rain Gauge
	OTH-NERG
	

	Rainfall at East AWWTP

FL0021865
	Inches
	Maximum
	Report
	Report
	-
	-
	Continuous

(Daily Reading)
	Rain Gauge
	OTH-SWRG
	


I. RECLAIMED WATER AND EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

A.
Reuse and Land Application Systems (continued)
2.  During the period beginning on the issuance date and lasting through the expiration date of this permit, the permittee is authorized to direct reclaimed water to Reuse System R-002.  Such reclaimed water shall be limited and monitored by the permittee as specified below:

	Total System
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (Total Flow, Pinellas County William E. Dunn MRS)

To R-002
	MGD
	Maximum
	3.0
	Report
	-
	-
	Monthly
	Calculation
	FLW-05
	See Cond.I.A.4


	Total System Inflows
	
	
	Reclaimed Water Limitations
	Monitoring Requirements
	

	Parameter
	Units
	Max/Min
	Annual

Average
	Monthly

Average
	Weekly

Average
	Single Sample
	Monitoring Frequency
	Sample Type
	Monitoring Location Site Number
	Notes

	Flow (Marshall Street AWWTP)

FL0021857
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-02
	See Cond.I.A.4

	Flow (Northeast AWWTP)

FL0128937
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-03
	See Cond.I.A.4

	Flow (East AWWTP)

FL0021865
	MGD
	Maximum
	Report*
	Report
	-
	-
	Continuous
	Meter
	FLW-04
	See Cond.I.A.4


* The permitted Annual Average Daily Flow (AADF) into the City of Clearwater Master Reuse System for each individual source facility is contained in the corresponding treatment facility permit.

3. Reclaimed water samples shall be taken at the monitoring site locations listed in Permit Condition I. A.  1. and as described below:

Total Public Access Master Reuse System
	Monitoring Location 
	Description of Monitoring Location

	FLW-01
	Total flow to R-001, FLW-01 = FLW-02 + FLW-03 + FLW-04

	FLW-05
	Total flow to R-002, FLW-01 = FLW-02 + FLW-03 + FLW-04


Inflows to the City of Clearwater Master Reuse System

	Monitoring Location 
	Description of Monitoring Location

	FLW-02
	Metered flow from the Marshall Street AWWTP

	FLW-03
	Metered flow from the Northeast AWWTP

	FLW-04
	Metered flow from the East AWWTP



Additional Monitoring

	Monitoring Location 
	Description of Monitoring Location

	OTH-MSRG
	Rain Gauge Located at Marshall Street AWWTF

	OTH-NERG
	Rain Gauge Located at Northeast AWWTF

	OTH-ERG
	Rain Gauge Located at East AWWTF 


4.  Recording flow meters and totalizers shall be utilized to measure flow and calibrated at least annually.  [62-601.200(17) and .500(6)]  
5.  The source treatment facilities shall be operated in accordance with all approved operating protocols.      Only reclaimed water that meets the criteria established in the approved operating protocol(s) may be released to system storage or to the reuse system.  Reclaimed water that fails to meet the criteria in the approved operating protocol(s) shall not be introduced into the master reuse system but stored and retreated at the source facility or directed to another permitted reuse system capable of disposing the reject water. The operating protocol(s) shall be reviewed and updated periodically to ensure continuous compliance with the minimum treatment and disinfection requirements.  Updated operating protocols shall be submitted to the Department for review and approval upon revision of the operating protocol(s) and with each permit application.  [62-610.320(6) and 62-610.463(2)]  
6.  Parameters which must be monitored as a result of a surface water discharge shall be analyzed using a sufficiently sensitive method in accordance with 40 CFR Part 136.  Parameters which must be monitored as a result of a ground water discharge (i.e., underground injection or land application system) shall be analyzed in accordance with Chapter 62-601, F.A.C. [62-620.610(18)]
7.  The permittee shall provide safe access points for obtaining representative influent, reclaimed water, and effluent samples which are required by this permit. [62-601.500(5)]
8.  Monitoring requirements under this permit are effective on the first day of the second month following permit issuance.  Until such time, the permittee shall continue to monitor and report in accordance with previously effective permit requirements, if any.  During the period of operation authorized by this permit, the permittee shall complete and submit to the Department Discharge Monitoring Reports (DMRs) in accordance with the frequencies specified by the REPORT type (i.e., monthly, toxicity, quarterly, semiannual, annual, etc.) indicated on the DMR forms attached to this permit.  Monitoring results for each monitoring period shall be submitted in accordance with the associated DMR due dates below, unless specified elsewhere in the permit.
	REPORT Type
	Monitoring Period
	Due Date

	Monthly  
	first day of month – last day of month
	28th day of following month

	Quarterly
	January 1 - March 31
April 1 – June 30
July 1 – September 30 
October 1 – December 31 
	April 28
July 28
October 28
January 28

	Semiannual
	January 1 – June 30
July 1 – December 31 
	July 28
January 28

	Annual
	January 1 – December 31
	January 28 


DMRs shall be submitted for each required monitoring period including months of no discharge.  The permittee shall make copies of the attached DMR form(s) and shall submit the completed DMR form(s) to the Department postmarked by the twenty-eighth (28th) of the month following the month of operation at the addresses specified below: 

Originals to:

Florida Department of Environmental Protection

Wastewater Compliance Evaluation Section, Mail Station 3551

Twin Towers Office Building

2600 Blair Stone Road

Tallahassee, Florida  32399-2400

Copies to:

Florida Department of Environmental Protection

Domestic Wastewater Program

Southwest District Office

13051 North Telecom Parkway
Temple Terrace, Florida  33637-0926

[62-620.610(18)][62-601.300(1),(2), and (3)]
9.  The permittee shall submit an Annual Reuse Report using DEP Form 62-610.300(4)(a)2. on or before January 1 of each year.  [62-610.870(3)]
10.  The permittee shall maintain an inventory of storage systems.  The inventory shall be submitted to the Department at least 30 days before reclaimed water will be introduced into any new storage system.  The inventory of storage systems shall be attached to the annual submittal of the Annual Reuse Report.  [62-610.464(5)]
11.  Unless specified otherwise in this permit, all reports and other information required by this permit, including 24-hour notifications, shall be submitted to or reported to, as appropriate, the Department's Southwest District Office at the address specified below:

Southwest District Office

13051 North Telecom Parkway
Temple Terrace, Florida  33637-0926

Phone Number - 813-632-7600

FAX Number -   813-632-7662

Email – DWSWD@DEP.STATE.FL.US 
All FAX copies shall be followed by original copies.  All reports and other information shall be signed in accordance with the requirements of Rule 62-620.305, F.A.C.  [62-620.305]
12.  Discharge of reclaimed water to the pond listed in the table below for storage of reclaimed water in the   stormwater storage lake system, D-001, shall only occur when the elevation of the water in the pond is less than the corresponding control elevation listed in the table below.  A list of all days during a month on which discharges from the pond to the receiving water body occurred shall be attached to the DMR form.  For each day on which discharge occurred, the approximate number of hours of discharge shall be noted.  [62-610.830(1) and (3)]
	Monitoring Location 
	Name of Storage Pond/Description of Monitoring Location
	Control Elevation (ft. M.S.L.)
	Receiving Water Body

	D-001

STM-01


	Countryside Country Club Pond


	86.47


	Possum Creek


II.
RESIDUALS MANAGEMENT REQUIREMENTS 



This section is not applicable to this facility.

III.
GROUND WATER REQUIREMENTS

Construction Requirements

1. The permittee shall give at least 72-hours notice to the Department's Southwest District Office, prior to the installation of any monitoring wells detailed in this permit.  [62-4.070]   

2. The QUARTERLY sampling and analysis of all new ground water monitoring wells shall begin upon proper completion of the GWMP well system.  The wells shall be sampled for the parameters identified in Permit Condition III.5 and in accordance to the Department’s “Standard Operating Procedures For Laboratory Operations and Sample Collection Activities,” DEP-SOP-001/01, FS 2200 Ground water Sampling, January 1, 2002. [62-522.600(1) , (11)(a),  and (b)]
3. Prior to construction of new ground water monitoring wells, a soil boring shall be made at each new monitoring well location in order to establish the well depth and screen interval.  [62-522.900(3)]
4. Within thirty days after completion of construction of the ground water monitoring wells, a properly scaled figure depicting monitor well locations (active and abandoned) with identification numbers shall be submitted.   The figure shall also include (or attached) the monitoring well, top of casing and ground surface elevations referenced to National Geodetic Vertcal Datum (NGVD) to the nearest 0.1 foot, along with monitor well location latitude and longitude to the nearest 0.1 second. 62-610.412 (c)
5. Within thirty days after completion of construction of the ground water monitoring wells, well completion reports shall be sent to the Domestic Wastewater Section, FDEP Southwest District Office.  The information is to be submitted on the attached form for each well, DEP Form 62-522.900(3), Monitor Well Completion Report.  [62-522.900(3)]

6. In Districts where applicable, within 30 days of completion of construction of new ground water monitor wells, the Department requests that the permittee submit the following information for each monitor well :

      a.   A copy of the Florida Water Management District (WMD) , State of Florida Permit  Application to Construct, Repair, Modify or Abandon a Well, Form 41.10-410(1),  and

   b.  A copy of the WMD Well Completion Report, Form 41.10-410(2),  62-610.412(2)(b)   
7. Prior to the application of effluent to the reuse/disposal site, the permittee shall sample all new ground water monitoring wells for the Primary and Secondary Drinking Water parameters included in Rule 62-550, Florida Administrative Code, Public Drinking Water Systems (excluding asbestos, acrylamide dioxin, butachlor and epichlorohydrin), and EPA Methods 601 and 602. [62-520.400 and 62-520.420]  [62-522.300(1), and 62-522.600(3)(A)]
8. The permittee shall coordinate any expansion of the Part III reclaimed water reuse system with the Southwest District Domestic Waste Permitting Section and shall propose additional ground water monitoring that may be required due to such expansion.  All new ground water monitoring wells that may subsequently be required shall be identified in a revision to the GWMP and shall be installed within 90 days of Department approval of the GWMP revision.  The permittee shall apply for a major revision to this permit to incorporate the selected wells and to provide appropriate DMR section D pages. [62-522.600(11)(C) and 62-610.320(3)]  

Operational Requirements

2. For the Part III Public Access system, all ground water quality criteria specified in Chapter 62-520, F.A.C., shall be met at the edge of the zone of discharge.  The zone of discharge shall extend horizontally 100 feet from the application site or to user’s site property line, whichever is less, and vertically to the base of the surficial aquifer.  [62-520.200(23)]  [62-522.400 and 62-522.410]  

3. The ground water minimum criteria specified in Rule 62-520.400 F.A.C., shall be met within the zone of discharge.  [62-520.400 and 62-520.420(4)]
4. During the period of operation authorized by this permit, the permittee shall sample ground water in accordance with this permit and the approved ground water monitoring plan prepared in accordance with Rule 62-522.600, F.A.C.  [62-522.600][62-610.463, ]
5. The following monitoring wells shall be sampled in accordance with the monitoring frequencies specified in Permit Condition III.5. for Reuse System R-001.  Quarterly sampling must be reasonably spaced to be representative of potentially changing conditions.
	Monitoring Well ID
	Alternate Well Name and/or Description of Monitoring Location
	Aquifer Monitored
	New or

Existing

	MWI-01
	Countryside GC-MW-1
	Surficial
	existing

	MWB-06
	Jack Russell Stadium/North Greenwood – MW-6
	Surficial
	new

	MWI-07
	Jack Russell Stadium/North Greenwood – MW-7
	Surficial
	new

	MWI-03
	Countryside Sport Complex-MW-3
	Surficial
	existing

	MWC-04
	Clearwater Northeast AWTP-MW-4
	Surficial
	existing

	MWB-05
	Countryside GC North End-MW-5
	Surficial
	existing

	MWC-09
	Jack Russell Stadium/North Greenwood-MW-8
	Surficial
	new

	MWC-07
	Harbor Oaks-MW-10
	Surficial
	existing

	MWC-08
	Morningside-MW-11
	Surficial
	existing


MWB = Background;  MWI = Intermediate;  MWC = Compliance
[62-522.600][62-610.463]  

5. The following parameters shall be analyzed for each of the monitoring wells identified in Permit Condition III. 4:

	Parameter
	Compliance Well Limit
	Units
	Sample Type
	Monitoring Frequency

	Water Level Relative to NGVD
	Report
	FEET
	In-situ
	Quarterly

	Nitrogen, Nitrate, Total (as N)
	10
	MG/L
	Grab
	Quarterly

	Solids, Total Dissolved (TDS)
	500
	MG/L
	Grab
	Quarterly

	Arsenic, Total Recoverable
	10
	UG/L
	Grab
	Quarterly

	Chloride (as Cl)
	250
	MG/L
	Grab
	Quarterly

	Cadmium, Total Recoverable
	5
	UG/L
	Grab
	Quarterly

	Chromium, Total Recoverable
	100
	UG/L
	Grab
	Quarterly

	Lead, Total Recoverable
	15
	UG/L
	Grab
	Quarterly

	Coliform, Fecal
	4
	#/100ML
	Grab
	Quarterly

	pH*
	6.0 to 8.5
	SU
	In-situ
	Quarterly

	Sulfate, Total
	250
	MG/L
	Grab
	Quarterly

	Turbidity*
	Report
	NTU
	In-situ
	Quarterly

	Sodium, Total Recoverable
	160
	MG/L
	Grab
	Quarterly

	Specific Conductance*
	Report
	UMHO/CM
	In-situ
	Quarterly

	Temperature (C), Water*
	Report
	DEG.C
	In-situ
	Quarterly

	Oxygen, Dissolved  (DO)*
	Report
	MG/L
	In-situ
	Quarterly


* The field parameters shall be sampled per DEP–SOP-001/01, FS 2200 Groundwater Sampling, Figure FS 2200-2 Groundwater Purging Procedure and recorded on Form FD 9000-24, Groundwater Sampling Log (both documents attached to this permit).  The sampling logs shall be submitted with each groundwater Part D DMR. The field parameters to be reported on Part D of GW DMR shall be the last sample recorded on FD 9000-24. 

[62-522.600(11)(b)] [62-601.300(3), 62-601.700, and Figure 3 of 62-601][62-601.300(6)] [62-520.300(9)]
6. If the concentration for any constituent listed in Permit Condition III. 5. in the natural background quality of the ground water is greater than the stated maximum, or in the case of pH is also less than the minimum, the representative natural background quality shall be the prevailing standard.                  [62-520.420(2)]  

7. In accordance with Part D of Form 62-620.910(10), water levels shall be recorded before evacuating wells for sample collection.  Elevation references shall include the top of the well casing and land surface at each well site (in NGVD) at a precision of plus or minus 0.1 foot.                                       [62-610.463(3)(a)]  

8. Ground water monitoring wells shall be purged prior to sampling to obtain representative samples.  [62-601.700(5)]  

9. Analyses shall be conducted on unfiltered samples, unless filtered samples have been approved by the Department's Southwest District Office as being more representative of ground water conditions.      [62-520.300(9)]  

10. Ground water monitoring parameters shall be analyzed in accordance with Chapter 62-601, F.A.C.  [62-620.610(18)]  

11. Ground water monitoring test results shall be submitted on Part D of Form 62-620.910(10). For reuse or land application projects, results shall be submitted with the DMR for each month listed in the following schedule.  The submitted results shall be for each year during the period of operation allowed by this permit in accordance with Permit Condition I.B.7.  [62-522.600(10) and (11)(b)]  [62-601.300(3), 62.601.700, and Figure 3 of 62-601] [62-620.610(18)]  

	SAMPLE PERIOD
	REPORT DUE DATE

	January - March
	April 28

	April - June
	July 28

	July - September
	October 28

	October - December
	January 28


12. If any monitoring well becomes damaged or cannot be sampled for some reason, the permittee shall notify the Department's Southwest District Office immediately and a written report shall follow within seven days detailing the circumstances and remedial measures taken or proposed.   Repair or replacement of monitoring wells shall be approved in advance by the Department's Southwest District Office.  [62-522.600][62-4.070(3)]  

13. The Permittee shall provide verbal notice to the Department's Southwest District Office as soon as practical after discovery of a sinkhole within an area for the management or application of wastewater, wastewater residuals (sludges), or reclaimed water.  The Permittee shall immediately implement measures appropriate to control the entry of contaminants, and shall detail these measures to the Department's Southwest District Office in a written report within 7 days of the sinkhole discovery.  [62-4.070(3)]  

14. All piezometers and monitoring wells not part of the approved ground water monitoring plan are to be plugged and abandoned in accordance with Rule 62-532.500(4), F.A.C., unless there is intent for their future use.  [62-532.500(4)]  

IV.
ADDITIONAL REUSE AND LAND APPLICATION REQUIREMENTS

Part III Public Access System (R-001 & R-002)
1. Use of reclaimed water for reuse system R-001 is authorized within the general service area identified in detail in Appendix A of the permit application dated January 25, 2006.  The following uses of reclaimed water are authorized within this general service area:  Golf Courses, Residential Developments, Residential Irrigation,  Athletic Complexes and Parks, Other Landscape Irrigation, [62-620.630(10)(d)]
2. This reuse system,  R-001, includes the following major users (i.e., using 0.1 MGD or more of reclaimed water):

	User Name
	Capacity (mgd)
	Acreage

	Island Estates
	0.352
	91.0

	Clearwater Country Club
	0.252
	65.0

	Countryside Golf Course
	0.531
	137.0

	Chi Chi Rodriquez Golf Course
	0.182
	47.0

	North Clearwater Beach
	0.490
	126.0

	South Clearwater Beach
	0.197
	51.0

	Drew and Union Streets Residential
	0.415
	107.0

	North Greenwood
	0.672
	173.0

	Harbor Oaks
	1.784
	460.0

	Seville
	1.420
	366.0

	Sunset
	0.154
	40.0

	Del Oro Groves
	1.319
	340.0

	Sky Crest
	0.248
	319.0

	Driving Range
	0.182
	33.0

	South Betty/Glen Oaks
	0.310
	399.0

	Palmetto/CC Estates
	0.191
	246.0

	Clearwater Harbor
	0.161
	208.0

	YMCA
	0.241
	311.0

	Sylvan Abbey Cemetery
	0.303
	78.0

	Totals
	9.40
	3597.0


[62-610.800(5)][62-620.630(10)(b)]
3. In addition to the above Master Reuse System, R-001, the City of Clearwater may furnish up to 3.0 mgd AADF of reclaimed water to the Pinellas County by means of an interconnect as called out in paragraphs 1 through 9, “ Duties and Responsibilities of the City, Reclaimed Water Supply Agreement with the City of Clearwater” executed February 7, 2000, between the City of Clearwater and the Pinellas County Government.  At a transfer point to be agreed mutually, the reclaimed water will be transferred into the Pinellas County William E. Dunn WRF Master Reuse System (FLA12877)

4. New major users of reclaimed water (i.e., using 0.1 MGD or more) may be added to the reuse system using the general permit described in Rule 62-610.890, F.A.C., if the requirements in this rule are complied with.  Application for use of this general permit shall be made using Form 62-610.300(4)(a)1.  [62-610.890]
5. Cross-connections to the potable water system are prohibited.  [62-610.469(7)]
6. A cross-connection control program shall be implemented and/or remain in effect within the areas where reclaimed water will be provided for use.  [62-610.469(7)]
7. The permittee shall conduct inspections within the reclaimed water service area to verify proper connections, to minimize illegal cross connections, and to verify the proper use of reclaimed water.  Inspections are required when a customer first connects to the reuse distribution system.  Subsequent inspections are required as specified in the cross-connection control and inspection program.  [62-610.469(7)(h)]
8. If a cross-connection between the potable and reclaimed water systems is discovered, the permittee shall:

a.
Immediately discontinue potable water and/or reclaimed water service to the affected area.

b.
If the potable water system is contaminated, clear the potable water lines.

c.
Eliminate the cross-connection.

d.
Test the affected area for other possible cross-connections.

e.
Within 24 hours, notify the Southwest District Office's domestic wastewater and drinking water programs.

f.
Within 5 days of discovery of a cross-connection, submit a written report to the Department detailing: a description of the cross-connection, how the cross-connection was discovered, the exact date and time of discovery, approximate time that the cross-connection existed, the location, the cause, steps taken to eliminate the cross-connection, whether reclaimed water was consumed, and reports of possible illness, whether the drinking water system was contaminated and the steps taken to clear the drinking water system, when the cross-connection was eliminated, plan of action for testing for other possible cross-connections in the area, and an evaluation of the cross-connection control and inspection program to ensure that future cross-connections do not occur.  [62-555.350(3) and 62-555.360][62-620.610(20)]
9. Maximum obtainable separation of reclaimed water lines and potable water lines shall be provided and the minimum separation distances specified in Rule 62-610.469(7), F.A.C., shall be provided.  Reuse facilities shall be color coded or marked.  Underground piping which is not manufactured of metal or concrete shall be color coded using Pantone Purple 522C using light stable colorants.  Underground metal and concrete pipe shall be color coded or marked using purple as the predominant color.  [62-610.469(7)]
10. In constructing reclaimed water distribution piping, the permittee shall maintain a 75-foot setback distance from a reclaimed water transmission facility to public water supply wells.  No setback distances are required to other potable water supply wells or to any nonpotable water supply wells.  [62-610.471(3)]
11. A setback distance of 75 feet shall be maintained between the edge of the wetted area and potable water supply wells, unless the utility adopts and enforces an ordinance prohibiting potable water supply wells within the reuse service area.  No setback distances are required to any nonpotable water supply well, to any surface water, to any developed areas, or to any private swimming pools, hot tubs, spas, saunas, picnic tables, barbecue pits, or barbecue grills.  [62-610.471(1), (2), (5), and (7)]
12. Reclaimed water shall not be used to fill swimming pools, hot tubs, or wading pools.  [62-610.469(4)]
13. Low trajectory nozzles, or other means to minimize aerosol formation shall be used within 100 feet from outdoor public eating, drinking, or bathing facilities.  [62-610.471(6)]
14. A setback distance of 100 feet shall be maintained from indoor aesthetic features using reclaimed water to adjacent indoor public eating and drinking facilities.  [62-610.471(8)]
15. The public shall be notified of the use of reclaimed water.  This shall be accomplished by posting of advisory signs in areas where reuse is practiced, notes on scorecards, or other methods.  [62-610.468(2)]
16. All new advisory signs and labels on vaults, service boxes, or compartments that house hose bibbs along with all labels on hose bibbs, valves, and outlets shall bear the words “do not drink” and “no beber” along with the equivalent standard international symbol.  In addition to the words “do not drink” and “no beber,” advisory signs posted at storage ponds and decorative water features shall also bear the words “do not swim” and “no nadar” along with the equivalent standard international symbols.  Existing advisory signs and labels shall be retrofitted, modified, or replaced in order to comply with the revised wording requirements.  [62-610.468 & 62-610.469]
17. The permittee shall ensure that users of reclaimed water are informed about the origin, nature, and characteristics of reclaimed water; the manner in which reclaimed water can be safely used; and limitations on the use of reclaimed water. Notification is required at the time of initial connection to the reclaimed water distribution system and annually after the reuse system is placed into operation.  A description of on-going public notification activities shall be included in the Annual Reuse Report.  [62-610.468(6)]
18. Routine aquatic weed control and regular maintenance of storage pond embankments and access areas are required.  [62-610.414 & 62-610.464]
19. Overflows from emergency discharge facilities on storage ponds shall be reported as an abnormal event to the Department's Southwest District Office within 24 hours of an occurrence.  The provisions of Rule 62-610.800(9), F.A.C., shall be met.  [62-610.800(9)]
V. OPERATION AND MAINTENANCE REQUIREMENTS

1.  During the period of operation authorized by this permit, the City of Clearwater Master Reuse System shall be operated under the overall supervision of the City of Clearwater Public Utilities Department and, at minimum, daily supervision by a wastewater superintendent, certified in accordance with Chapter 62-602, F.A.C. and in accordance with the requirements of the approved Operating Protocol’s for each of the source facilities. 

2.  The lead operator shall be employed at the plant full time.  “Full time” shall mean at least 4 days per week, working a minimum of 35 hours per week, including leave time.  A certified operator shall be on-site and in charge of each required shift and for periods of required staffing time when the lead operator is not on-site.  An operator meeting the lead operator classification level of the plant shall be available during all periods of plant operation.  “Available” means able to be contacted as needed to initiate the appropriate action in a timely manner.  [62-699.311(10), (5) and (1)]
3.  The application to renew this permit shall include a detailed operation and maintenance performance report prepared in accordance with Rule 62-600.735, F.A.C.  [62-600.735(1)]
4.  The permittee shall maintain the following records and make them available for inspection at the City of Clearwater Public Utilities administrative offices.

a.
Records of all compliance monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation and a copy of the laboratory certification showing the certification number of the laboratory, for at least three years from the date the sample or measurement was taken;

b.
Copies of all reports required by the permit for at least three years from the date the report was prepared;

c.
Records of all data, including reports and documents, used to complete the application for the permit for at least three years from the date the application was filed;

d.
Monitoring information, including a copy of the laboratory certification showing the laboratory certification number, related to the residuals use and disposal activities for the time period set forth in Chapter 62-640, F.A.C., for at least three years from the date of sampling or measurement;

e.
A copy of the current permit;

f.
A copy of the current operation and maintenance manual as required by Chapter 62-600,. F.A.C.;

g.
A copy of the facility record drawings;

h.
Copies of the licenses of the current certified operators; and 

i.
Copies of  the logs and schedules showing plant operations and equipment maintenance for three years from the date of the logs or schedules.  The logs shall, at a minimum, include identification of the plant; the signature and certification number of the operator(s) and the signature of the person(s) making any entries; date and time in and out; specific operation and maintenance activities; tests performed and samples taken; and major repairs made. The logs shall be maintained on-site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed.


[62-620.350]
VI.
SCHEDULES



This section does not apply to the facility.

VII.  INDUSTRIAL PRETREATMENT PROGRAM REQUIREMENTS

This section does not apply to this permit.  

VIII.  OTHER SPECIFIC CONDITIONS

1. If the permittee wishes to continue operation of this wastewater facility after the expiration date of this permit, the permittee shall submit an application for renewal, using Department Forms 62-620.910(1) and (2), no later than one-hundred and eighty days (180) prior to the expiration date of this permit.  [62-620.410(5)]
2. Florida water quality criteria and standards shall not be violated as a result of any discharge or land application of reclaimed water or residuals from this facility.  [62-610.850(1)(a) and (2)(a)]
3. In the event that the treatment facilities or equipment no longer function as intended, are no longer safe in terms of public health and safety, or odor, noise, aerosol drift, or lighting adversely affects neighboring developed areas at the levels prohibited by Rule 62-600.400(2)(a), F.A.C., corrective action (which may include additional maintenance or modifications of the permitted facilities) shall be taken by the permittee.  Other corrective action may be required to ensure compliance with rules of the Department.  Additionally, the treatment, management, use or land application of residuals shall not cause a violation of the odor prohibition in Rule 62-296.320(2), F.A.C.  [62-600.410(8) and 62-640.400(6)]
4. The deliberate introduction of stormwater in any amount into collection/transmission systems designed solely for the introduction (and conveyance) of domestic/industrial wastewater; or the deliberate introduction of stormwater into collection/transmission systems designed for the introduction or conveyance of combinations of storm and domestic/industrial wastewater in amounts which may reduce the efficiency of pollutant removal by the treatment plant is prohibited, except as provided by Rule 62-610.472, F.A.C.  [62-604.130(3)]
5. Collection/transmission system overflows shall be reported to the Department in accordance with Permit Condition IX. 20.  [62-604.550]  [62-620.610(20)]
6. The operating authority of a collection/transmission system and the permittee of a treatment plant are prohibited from accepting connections of wastewater discharges which have not received necessary pretreatment or which contain materials or pollutants other than normal domestic wastewater constituents:

a.
Which may cause fire or explosion hazards; or

b.
Which may cause excessive corrosion or other deterioration of wastewater facilities due to chemical action or pH levels; or

c.
Which are solid or viscous and obstruct flow or otherwise interfere with wastewater facility operations or treatment; or

d. Which result in the wastewater temperature at the introduction of the treatment plant exceeding 40oC or otherwise inhibiting treatment: or

e. Which result in the presence of toxic gases, vapors, or fumes that may cause worker health and safety problems.

[62-604.130(54)]
7. The treatment facility, storage ponds, rapid infiltration basins, and/or infiltration trenches shall be enclosed with a fence or otherwise provided with features to discourage the entry of animals and unauthorized persons.  [62-600.400(2)(b)]
8. Screenings and grit removed from the wastewater facilities shall be collected in suitable containers and hauled to a Department approved Class I landfill or to a landfill approved by the Department for receipt/disposal of screenings and grit.  [62-701.300(1)(a)]
9. The permittee shall provide adequate notice to the Department of the following:

a.
Any new introduction of pollutants into the facility from an industrial discharger which would be subject to Chapter 403, F.S., and the requirements of Chapter 62-620, F.A.C. if it were directly discharging those pollutants; and

b.
Any substantial change in the volume or character of pollutants being introduced into that facility by a source which was identified in the permit application and known to be discharging at the time the permit was issued.

Adequate notice shall include information on the quality and quantity of effluent introduced into the facility and any anticipated impact of the change on the quantity or quality of effluent or reclaimed water to be discharged from the facility.

[62-620.625(2)]
IX.
GENERAL CONDITIONS

1.
The terms, conditions, requirements, limitations and restrictions set forth in this permit are binding and enforceable pursuant to Chapter 403, Florida Statutes.  Any permit noncompliance constitutes a violation of Chapter 403, Florida Statutes, and is grounds for enforcement action, permit termination, permit revocation and reissuance, or permit revision.  [62-620.610(1)]

2.
This permit is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviations from the approved drawings, exhibits, specifications or conditions of this permit constitute grounds for revocation and enforcement action by the Department.  [62-620.610(2)]
3.
As provided in Subsection 403.087(6), F.S., the issuance of this permit does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor authorize any infringement of federal, state, or local laws or regulations.  This permit is not a waiver of or approval of any other Department permit or authorization that may be required for other aspects of the total project which are not addressed in this permit.  [62-620.610(3)]
4.
This permit conveys no title to land or water, does not constitute state recognition or acknowledgment of title, and does not constitute authority for the use of submerged lands unless herein provided and the necessary title or leasehold interests have been obtained from the State.  Only the Trustees of the Internal Improvement Trust Fund may express State opinion as to title.  [62-620.610(4)]

5.
This permit does not relieve the permittee from liability and penalties for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source; nor does it allow the permittee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department.  The permittee shall take all reasonable steps to minimize or prevent any discharge, reuse of reclaimed water, or residuals use or disposal in violation of this permit which has a reasonable likelihood of adversely affecting human health or the environment.  It shall not be a defense for a permittee in an enforcement action that it would have been necessary to halt or reduce the permitted activity in order to maintain compliance with the conditions of this permit.  [62-620.610(5)]
6.
If the permittee wishes to continue an activity regulated by this permit after its expiration date, the permittee shall apply for and obtain a new permit.  [62-620.610(6)]
7.
The permittee shall at all times properly operate and maintain the facility and systems of treatment and control, and related appurtenances, that are installed and used by the permittee to achieve compliance with the conditions of this permit.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to maintain or achieve compliance with the conditions of the permit.  [62-620.610(7)]

8.
This permit may be modified, revoked and reissued, or terminated for cause.  The filing of a request by the permittee for a permit revision, revocation and reissuance, or termination, or a notification of planned changes or anticipated noncompliance does not stay any permit condition.  [62-620.610(8)]

9.
The permittee, by accepting this permit, specifically agrees to allow authorized Department personnel, including an authorized representative of the Department and authorized EPA personnel, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated, to:

a.
Enter upon the permittee’s premises where a regulated facility, system, or activity is located or conducted, or where records shall be kept under the conditions of this permit;

b.
Have access to and copy any records that shall be kept under the conditions of this permit;

c.
Inspect the facilities, equipment, practices, or operations regulated or required under this permit; and

d.
Sample or monitor any substances or parameters at any location necessary to assure compliance with this permit or Department rules.


[62-620.610(9)]

10.
In accepting this permit, the permittee understands and agrees that all records, notes, monitoring data, and other information relating to the construction or operation of this permitted source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the permitted source arising under the Florida Statutes or Department rules, except as such use is proscribed by Section 403.111, Florida Statutes, or Rule 62-620.302, Florida Administrative Code.  Such evidence shall only be used to the extent that it is consistent with the Florida Rules of Civil Procedure and applicable evidentiary rules.  [62-620.610(10)]

11.
When requested by the Department, the permittee shall within a reasonable time provide any information required by law which is needed to determine whether there is cause for revising, revoking and reissuing, or terminating this permit, or to determine compliance with the permit.  The permittee shall also provide to the Department upon request copies of records required by this permit to be kept.  If the permittee becomes aware of relevant facts that were not submitted or were incorrect in the permit application or in any report to the Department, such facts or information shall be promptly submitted or corrections promptly reported to the Department.  [62-620.610(11)]

12.
Unless specifically stated otherwise in Department rules, the permittee, in accepting this permit, agrees to comply with changes in Department rules and Florida Statutes after a reasonable time for compliance; provided, however, the permittee does not waive any other rights granted by Florida Statutes or Department rules.  A reasonable time for compliance with a new or amended surface water quality standard, other than those standards addressed in Rule 62-302.500, F.A.C., shall include a reasonable time to obtain or be denied a mixing zone for the new or amended standard.  [62-620.610(12)]

13.
The permittee, in accepting this permit, agrees to pay the applicable regulatory program and surveillance fee in accordance with Rule 62-4.052, F.A.C.  [62-620.610(13)]

14.
This permit is transferable only upon Department approval in accordance with Rule 62-620.340, F.A.C.  The permittee shall be liable for any noncompliance of the permitted activity until the transfer is approved by the Department.  [62-620.610(14)]

15.
The permittee shall give the Department written notice at least 60 days before inactivation or abandonment of a wastewater facility and shall specify what steps will be taken to safeguard public health and safety during and following inactivation or abandonment.  [62-620.610(15)]

16.
The permittee shall apply for a revision to the Department permit in accordance with Rules 62-620.300 and the Department of Environmental Protection Guide to Wastewater Permitting at least 90 days before construction of any planned substantial modifications to the permitted facility is to commence or with Rule 62-620.325(2) for minor modifications to the permitted facility.  A revised permit shall be obtained before construction begins except as provided in Rule 62-620.300, F.A.C.  [62-620.610(16)]
17.
The permittee shall give advance notice to the Department of any planned changes in the permitted facility or activity which may result in noncompliance with permit requirements.  The permittee shall be responsible for any and all damages which may result from the changes and may be subject to enforcement action by the Department for penalties or revocation of this permit.  The notice shall include the following information:

a.
A description of the anticipated noncompliance;

b.
The period of the anticipated noncompliance, including dates and times; and

c.
Steps being taken to prevent future occurrence of the noncompliance.


[62-620.610(17)]

18. 
Sampling and monitoring data shall be collected and analyzed in accordance with Rule 62-4.246, Chapters 62-160 and 62-601, F.A.C., and 40 CFR 136, as appropriate.

a.
Monitoring results shall be reported at the intervals specified elsewhere in this permit and shall be reported on a Discharge Monitoring Report (DMR), DEP Form 62-620.910(10), or as specified elsewhere in the permit.

b.
If the permittee monitors any contaminant more frequently than required by the permit, using Department approved test procedures, the results of this monitoring shall be included in the calculation and reporting of the data submitted in the DMR.

c.
Calculations for all limitations which require averaging of measurements shall use an arithmetic mean unless otherwise specified in this permit.

d.
Except as specifically provided in Rule 62-160.300, F.A.C., any laboratory test required by this permit shall be performed by a laboratory that has been certified by the Department of Health Environmental Laboratory Certification Program (DOH ELCP).  Such certification shall be for the matrix, test method and analyte(s) being measured to comply with this permit.  For domestic wastewater facilities, testing for parameters listed in Rule 62-160.300(4), F.A.C., shall be conducted under the direction of a certified operator.

e.
Field activities including on-site tests and sample collection shall follow the applicable standard operating procedures described in DEP-SOP-001/01 adopted by reference in Chapter 62-160, F.A.C.  

f.
Alternate field procedures and laboratory methods may be used where they have been approved in accordance with Rules 62-160.220 and 62-160.330, F.A.C.



[62-620.610(18)]
19.
Reports of compliance or noncompliance with, or any progress reports on, interim and final requirements contained in any compliance schedule detailed elsewhere in this permit shall be submitted no later than 14 days following each schedule date.  [62-620.610(19)]

20.
The permittee shall report to the Department any noncompliance which may endanger health or the environment.  Any information shall be provided orally within 24 hours from the time the permittee becomes aware of the circumstances.  A written submission shall also be provided within five days of the time the permittee becomes aware of the circumstances.  The written submission shall contain:  a description of the noncompliance and its cause; the period of noncompliance including exact dates and time, and if the noncompliance has not been corrected, the anticipated time it is expected to continue; and steps taken or planned to reduce, eliminate, and prevent recurrence of the noncompliance.

a.
The following shall be included as information which must be reported within 24 hours under this condition:

1.
Any unanticipated bypass which causes any reclaimed water or effluent to exceed any permit limitation or results in an unpermitted discharge,

2.
Any upset which causes any reclaimed water or the effluent to exceed any limitation in the permit,

3.
Violation of a maximum daily discharge limitation for any of the pollutants specifically listed in the permit for such notice, and

4.
Any unauthorized discharge to surface or ground waters.

b.
Oral reports as required by this subsection shall be provided as follows:

1.
For unauthorized releases or spills of treated or untreated wastewater reported pursuant to subparagraph a.4 that are in excess of 1,000 gallons per incident, or where information indicates that public health or the environment will be endangered, oral reports shall be provided to the Department by calling the STATE WARNING POINT TOLL FREE NUMBER (800) 320-0519, as soon as practical, but no later than 24 hours from the time the permittee becomes aware of the discharge. The permittee, to the extent known, shall provide the following information to the State Warning Point:

a) Name, address, and telephone number of person reporting;

b) Name, address, and telephone number of permittee or responsible person for the discharge; 

c) Date and time of the discharge and status of discharge (ongoing or ceased); 

d) Characteristics of the wastewater spilled or released (untreated or treated, industrial or domestic wastewater);

e) Estimated amount of the discharge;

f) Location or address of the discharge; 

g) Source and cause of the discharge; 

h) Whether the discharge was contained on-site, and cleanup actions taken to date; 

i) Description of area affected by the discharge, including name of water body affected, if any; and  

j) Other persons or agencies contacted.

2.
Oral reports, not otherwise required to be provided pursuant to subparagraph b.1 above,  shall be provided to the Department within 24 hours from the time the permittee becomes aware of the circumstances. 

c.
If the oral report has been received within 24 hours, the noncompliance has been corrected, and the noncompliance did not endanger health or the environment, the Department shall waive the written report.


[62-620.610(20)]

21.
The permittee shall report all instances of noncompliance not reported under Permit Conditions IX. 18. and 19. of this permit at the time monitoring reports are submitted.  This report shall contain the same information required by Permit Condition IX. 20 of this permit.  [62-620.610(21)]

22.
Bypass Provisions.

a.
Bypass is prohibited, and the Department may take enforcement action against a permittee for bypass, unless the permittee affirmatively demonstrates that:

1.
Bypass was unavoidable to prevent loss of life, personal injury, or severe property damage; and 

2.
There were no feasible alternatives to the bypass, such as the use of auxiliary treatment facilities, retention of untreated wastes, or maintenance during normal periods of equipment downtime.  This condition is not satisfied if adequate back-up equipment should have been installed in the exercise of reasonable engineering judgment to prevent a bypass which occurred during normal periods of equipment downtime or preventive maintenance; and

3.
The permittee submitted notices as required under Permit Condition IX. 22. b. of this permit.

b.
If the permittee knows in advance of the need for a bypass, it shall submit prior notice to the Department, if possible at least 10 days before the date of the bypass.  The permittee shall submit notice of an unanticipated bypass within 24 hours of learning about the bypass as required in Permit Condition IX. 20. of this permit.  A notice shall include a description of the bypass and its cause; the period of the bypass, including exact dates and times; if the bypass has not been corrected, the anticipated time it is expected to continue; and the steps taken or planned to reduce, eliminate, and prevent  recurrence of the bypass.

c.
The Department shall approve an anticipated bypass, after considering its adverse effect, if the permittee demonstrates that it will meet the three conditions listed in Permit Condition IX. 22. a. 1. through 3. of this permit.

d.
A permittee may allow any bypass to occur which does not cause reclaimed water or effluent limitations to be exceeded if it is for essential maintenance to assure efficient operation.  These bypasses are not subject to the provisions of Permit Condition IX. 22. a. through c. of this permit.


[62-620.610(22)]

23.
Upset Provisions

a.
A permittee who wishes to establish the affirmative defense of upset shall demonstrate, through properly signed contemporaneous operating logs, or other relevant evidence that:

1.
An upset occurred and that the permittee can identify the cause(s) of the upset;

2.
The permitted facility was at the time being properly operated;

3.
The permittee submitted notice of the upset as required in Permit Condition IX. 20. of this permit; and

4.
The permittee complied with any remedial measures required under Permit Condition IX. 5. of this permit.

b.
In any enforcement proceeding, the permittee seeking to establish the occurrence of an upset has the burden of proof.

c.
Before an enforcement proceeding is instituted, no representation made during the Department review of a claim that noncompliance was caused by an upset is final agency action subject to judicial review.

[62-620.610(23)]

Executed in Hillsborough County, Florida.

STATE OF FLORIDA DEPARTMENT OF ENVIRONMENTAL PROTECTION

____________________________________

Jeffry S. Greenwell, P.E.

Water Facilities Administrator







Southwest District Office

PA File No. FL0186261-003-DW1R/NR

2
PA File No. FL0186261-003-DW1R/NR


