## Instructions
Below are data field definitions, and codes to be used when completing the incident tracking spreadsheet.
*District staff should verify / correct the data in any of the fields listed above should more current / accurate information become available.
Data Fields 1-15 (in gray) are generally entered by Tallahassee staff for the incidents that are reported to the SWP. Fields highlighted in Blue Text are the REQUIRED fields for all incidents including those reported directly to the Disitrict office.
Data Field Definitions
1 | SWP ID | State Warning Point Tracking Number, if none, leave blank
2 | Date | Date the incident was reported to the DEP or SWP
3 | Time | Time incident was reported
4 | County | County where the incident occurred
5 | District | District the incident occurred in
6 | Incident Time | Time the incident occurred/began
7 | Caller Name | Name of person reporting incident
8 | Affiliation | Affiliation of person reporting incident (utility, county, private citizen, etc.) NOTE: if caller/utility is reporting spill associated with another entity (ex: private L/S, contractor, etc.) please update "Responsible Party" to reflect who is ultimately responsible, if known
9 | Description | Callers description of incident
10 | Incident Location | Where the incident occurred (street address, L/S, etc.)
11 | Cleanup Actions | Cleanup Actions taken by the responsible party and/or emergency response
12 | Facility Type | Industrial (IW) or leave blank if Domestic (DW)
13 | Wastewater Characteristics | Indicate treatment level of wastewater "Partially" treated or fully "Treated" "Bio-solids" "Reclaim (Part III) Water" (leave blank if raw sewage or untreated)
14 | Spill Amount | Amount released in gallons
15 | Cause | Cause of incident (See code table above)
16 | Volume Recovered | Amount of spill recovered
17 | Water Body Affected | Name of Water Body affected (blank indicates ground surface/ground water)
18 | Responsible Party | Responsible party of spill (if different from the affiliation of person reporting incident)
19 | Follow-up Activities | Followup activities conducted (ie inspections, sampling, meetings etc)
20 | FAC ID | ID Number of associated facility
21 | DEP Lead Staff | Staff person assigned or agency delegated (ie DOH, County Health Dept)
22 | DEP Action | Enforcement Type (ie Warning Letter, Non-Compliance letter, Consent Order etc)
23 | Tracking # | Tracking Number assigned by district or OGC/docket#
24 | Penalty Amt Assessed | Penalty Amount assessed for the incident
Code | Cause
Unknown | Unknown /Cause not reported
Accident | Auto Accident/3rd Party Actions/Vandalism
Break-in-Line | Break in Line
Equipment | Equipment Malfunction
FOG | Clog as a result of Fats, Oils and/or Grease
Blockage | Blockage other than FOG, incl'd roots, debris, etc.
Power | Power failure or surge
Contractor | Contractor caused break
Overflow | Overflow
Rain | Heavy Rains/Infiltration of Stormwater
Negligence | Negligence/Intentional/Error
Repair | Repair work
Hauling | Hauling/Sludge related
On-site | Any incident that occurs & remains w/n the confines of the treatment facility
Vessel | Vessel or boating release
Security | Security issue or breach
The Summary-Graphs spreadsheet is updated automatically by the data contained in the Incident-Tracking sheet.

## Incident-Tracking
SWP ID | Date | Time | County | District | Incident Time | Caller Name | Affiliation | Description | Incident Location | Cleanup Actions | Fac Type (IW, Blank=DW) | Wastewater Characteristics | Spill Amount (in gals) | Cause | Volume Recovered | Surface Water Body Affected | Responsible Party (if diff from affiliation) | Follow-up Activities | FAC ID or Utility Name | Lead Staff | DEP Action | Tracking # | Penalty Amt Assessed | Comments | City | Specific Cause | closed
28 | 2013-01-02 | 613p | Lee | SD | 1/2/2013 17:00 ET | Bonnie Pringle | Gasparilla Island | Caller is reporting a wastewater spill of an undetermined amount in Boca Grande entering a storm drain that discharges to Boca Grande Bayou. Caller stated that the wastewater is coming out of the ground from a gravity line. UPDATE 1/4/13: Samples taken upstream and downstream of storm outfall. Fecal coliforms below limits. | East Railroad Ave. & 5th St, Boca Grande | in-progress |  |  | unknown | blockage |  | storm drain to Boca Grande Bayou | Gasparilla Island | samples taken
| 2013-01-02 | 324p | Lee | SD | 1/2/2013. | Jon Kio | City of Cape Coral | Crack in 12" forcemain caused 750 gallons to be spilled. Spill contained and removed w/vac truck. Line repaired, area disinfected with lime. | 3622 Santa Barbara Blvd, Cape Coral | vac & lime |  |  | 750 | break-in-line |  |  | City of Cape Coral
45 | 2013-01-03 | 324p | DeSoto | SD | 1/3/2013 07:00 ET | Alex Shannon | DeSoto Co Utilities | Caller reported that 10,000 gallons of raw sewage was released due to a broken Air Release Valve in Arcadia. The release did not affect any storm water systems or surface waters. Clean up actions are planned. | U.S. 17 & Collins Street, Arcadia | planned |  |  | 10000 | break-in-line |  |  | DeSoto Co Utilities
46 | 2013-01-03 | 348p | Sarasota | SD | 1/3/2013 15:48 ET | Gerald Boyce | City of Sarasota | Caller reported that 30,000 gallons of raw sewage spilled due to a broken air release valve in Sarasota. The spill did affect a unnamed canal. Clean up actions are in progress. UPDATE: As of 1/4/13, samples collected from bayou are below limits for fecal coliforms. | 904 Pomelo Avenue, Sarasota | lime |  |  | 30000 | break-in-line | 18000 | Hudson Bay | City of Sarasota | signs posted, samples taken
77 | 2013-01-05 | 213p | Lee | SD | 1/5/2013 14:13 ET | Jon Kio | City of Cape Coral | Between 35,000 and 40,000 gallons of raw sewage spilled due to a break in a force main in Cape Coral. A nearby storm drain that is believed to discharge into a retention pond was affected. Clean up actions were conducted. | 610 SE 26th Street, Cape Coral | vac & lime |  |  | 40000 | break-in-line |  | retention pond | City of Cape Coral
167 | 2013-01-10 | 324p | Sarasota | SD | 1/10/2013 14:00 ET | Trisha Niharg | Venice Gardens WRF | Caller reports a release of 3,000 gallons of untreated wastewater in Venice due to loss of power at control panel. Caller stated that the release did not affect any storm water systems or surface waters. Clean up actions were taken. | 375 Venice East BLVD, Venice | vac & lime |  |  | 3000 | power | 1000 |  | Sarasota County Utilities
| 2013-01-10 | 230p | Sarasota | SD | 1/10/2013. | Bob Hogan | Venice Gardens | 200 to 300 gallons spilled from Plantation master LS due to power failure. Power restored. | 921 Woodbridge Dr, Venice |  |  |  | 300 | power |  |  | Venice Gardens
183 | 2013-01-11 | 1231p | Sarasota | SD | 1/11/2013 11:30 ET | Steve Bothast | Sarasota County Public Utilities | Sarasota County Public Utilities reports a Wastewater Release in Venice. Approximately 2,000 gallons of raw wastewater was released from a manhole near the Lift Station due to a blockage. Repairs and Clean-up actions have been completed. UPDATE: All samples below limits for fecal coliforms. | 262 Cerromar Drive, Venice | vac & lime |  |  | 2000 | blockage | 6000 | retention pond | Sarasota County Utilities | samples taken
196 | 2013-01-12 | 101p | Lee | SD | 1/12/2013 13:01 ET | Lina Quintero | US Water-Del Prado WWTP | Caller reports a release of 9,000 gallons of wastewater due to a broken air release valve in North Ft. Myers. No storm water systems and no surface waters were affected. Clean up actions have been taken. | 10291 Bay Shore Rd, North Fort Myers | vac & lime |  |  | 9000 | accident | 8000 |  | US Water
228 | 2013-01-14 | 131p | Charlotte | SD | 1/14/2013 09:30 ET | Mike | Charlotte County Utilities | Charlotte County Utilities is reporting a wastewater spill of 4,000 gallons in Port Charlotte. The spill entered Eastland Waterway. Clean up is in progress. | Biscayne Dr. & Wyandotte Ave, Port Charlotte | disinfection |  |  | 4000 | accident |  | Eastland Waterway | Charlotte County Utilities
| 2013-01-15 | 555p | Sarasota | SD | 1/15/2013 09:00 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 15 gallons overflowed from manhole due to grease blockage in mainline. Blockage cleared, affected area washed down and treated with lime. | 2159 Bay Street, Sarasota | vac & lime |  |  | 15 | FOG |  |  | City of Sarasota
| 2013-01-15 | 958p | Collier | SD | 1/13/2013. | Ray See | Collier County-North | 100 gallons overflowed from 2 manholes onto the road and into a storm drain due to a blockage in the gravity line. Vac truck cleared line, area was disinfected, educational public outreach conducted in area. | 2896 Tiburon Blvd, Naples | vac & disinfect |  |  | 100 | FOG | 20 |  | Collier County Collections
| 2013-01-16 | 1230p | Collier | SD | 1/15/2013 15:45 ET | Richard Orth | Collier County Pollution Control | 200 gallons overflowed from manhole due to grease blockage and flowed across parking lot into isolated stormwater lake. Blockage cleared by Sewer Viewer, affected area washed down with bleach solution. | 4058 Bayshore Dr, Naples | bleach |  |  | 200 | FOG |  |  | Linda Alvarez, Oceans 52 Apartment Homes
302 | 2013-01-18 | 320p | Sarasota | SD | 1/18/2013 11:00 ET | Teresa | Private Citizen | Concerned citizen reports illegal dumping of raw sewage in Sarasota. Caller states that the Responsible Party is draining his Septic Pump Truck directly into his backyard. Reporting Party has made contact with local Health Department, but nothing was ever done about this. The vehicle in question is an old, white Pump Truck with a red sewage tank on the back. | 8472 31st Court NE, Sarasota | unknown |  |  | unknown | negligence |  |  | Private Citizen
| 2013-01-18 | 306p | Collier | SD | 1/14/2013 13:00 ET | Danette Kinaszczuk | Collier County-North | Approx 300 gals of reclaimed water released due to leak in private irrigation line. Reclaimed water absorbed into surrounding grassy area. | 8776 Ventura Way, Naples | none |  | reclaimed | 300 | break-in-line |  |  | Collier County Utilities
| 2013-01-19 | 330p | Sarasota | SD | 1/19/2013. | Rick Newkirk | North Port Utilities | Approx 250-400 gals spilled from LS due to panel malfunction. Spill affected curb and gutter. Removed with vac truck and washed down. Panel repaired. | 2000 Villa Rd, North Port | vac |  |  | 400 | equipment |  |  | North Port Utilities
326 | 2013-01-20 | 1014a | Lee | SD | 1/19/2013 13:10 ET | Doug | US Water-Lehigh Acres WWTP | Caller is reporting a treated effluent spill of 270,000 gallons in Lehigh Acres. Caller states that a pipe had a hole in it causing the release. Repairs completed, samples taken. All samples under limits. | 601 Construction Ln., Lehigh Acres | none |  | treated | 270000 | break-in-line |  | Able Canal | US Water
353 | 2013-01-21 | 918p | Sarasota | SD | 1/21/2013 19:00 ET | Roy Lessig | Sarasota County Utilities | Caller reported that 14,000 gallons of raw sewage was released due to a backed up manhole in Sarasota. The release went into a storm drain that discharge into a retention pond, which leads to the Sarasota Bay. Clean up actions are in progress. UPDATE: Blockage cleared, stormwater vault pumped out, area disinfected with lime. | 4828 Peregrine Point Circle, Sarasota | vac & lime |  |  | 14000 | blockage | 28600 | stormdrain | Sarasota County Utilities
| 2013-01-22 | 102p | Sarasota | SD | 1/22/2013 07:30 ET | Don Hostetler | Aqua Utilities-Fruitville WWTP | Approx 200 gals MLSS leaked from RAS pump. Repairs completed, soda ash applied to spill. | Fruitville WWTP | soda ash |  | partially treated | 200 | onsite |  |  | Aqua Utilities
476 | 2013-01-28 | 601p | Collier | SD | 1/28/2013 18:01 ET | Debbie Lester |  | Caller reports a sewage spill of approximately 80-100 gallons in Naples. The spill is coming from a septic tank that was affected by private construction. It is unknown if any surface waters were affected. Caller requests a call back from DEP. | 4340 Pine Ridge Rd Extension, Naples | none |  |  | 100 | contractor |  |  | 0
| 2013-01-29 | 800a | Lee | SD | 1/28/2013. | Jerry May | Bonita Springs West WRF | 500 gallons spilled when a vehicle hit an ARV and broke it. ARV was repaired and area was disinfected with lime. | Old 41 Rd & Mediterra Dr, Bonita Springs | lime |  |  | 500 | accident |  |  | Bonita Springs Utilities
| 2013-01-31 | 915a | Lee | SD | 1/31/2013 07:30 ET | Jerry May | Bonita Springs West WRF | 20 gallons spilled from a cleanout opened by a customer. Sewage collected with vac truck, area limed. | 8881 Terrene Ct, Bonita Springs | vac & lime |  |  | 20 | accident |  |  | Bonita Springs Utilities
603 | 2013-02-03 | 1200p | Monroe | SD | 2/3/2013 13:22 ET | Ed Barham | Naval AirStation Key West | Naval Air Station Key West is reporting a wastewater spill on their base that is of an unknown quantity flowing into a canal. Caller stated that repairs are underway and clean up is planned. | Naval Air Station Key West | vac & disinfect |  |  | 200 | break-in-line |  |  | Naval AirStation Key West
604 | 2013-02-03 | 145p | Sarasota | SD | 2/3/2013 14:57 ET | Doug | Bee Ridge WRF | Caller is reporting a wastewater spill of 10,000 gallons in Sarasota. Caller advises that the spill is in drainage ditches and was caused by a blockage in the main line. Clean up is underway. UPDATE: Three manholes overflowed. Spill entered adjacent canal and stormwater pond. Blockage cleared, canal vacuumed up, roadways washed down and affected areas limed. Samples pulled and all under fecal coliform limits. | 4312 Dresden Ln. Sarasota | vac & lime |  |  | 10000 | blockage | 20000 |  | Sarasota County Utilities
628 | 2013-02-04 | 419p | Lee | SD | 2/2/2013 19:00 ET | Lina Quintero | US Water-Del Prado WWTP | Caller reports a reuse water spill of approximately 6,300 gallons in Ft. Myers. Butterfly valve failed causing reuse well to overflow. The spill occurred Saturday but the caller did not report it because the estimate of the spill was significantly less at the time of the incident. The spill was contained inside the facility. U.S. Water Services conducted the clean up. | 4100 Del Prado Blvd, North Fort Myers | none |  | reuse | 6300 | onsite |  |  | US Water
| 2013-02-04 | 340p | Collier | SD | 1/30/2013 10:30 ET | Jesse Komorny | Collier County-South | 30 gallons spilled during scheduled ARV removal/replacement by contractor (Quality Enterprises). Standing wastewater recovered and impacted area disinfected with bleach. | NE Corner of Mulberry & Fiddlers Creek Pkwy, Naples | vac & bleach |  |  | 30 | contractor | 20 |  | Collier County Utilities
| 2013-02-06 | 304p | Charlotte | SD | 2/6/2013 08:30 ET | Patrick Godwin | Utilities Inc-Sandalhaven WWTP | Breakers tripped at LS #6 causing 15 gallons total to overflow from 2 manholes. Reset breakers, washed down and disinfected with bleach and lime. | 6610 Gasparilla Pines Blvd, Englewood | bleach & lime |  |  | 15 | power |  |  | Utilities Inc.
| 2013-02-06 | 100p | Sarasota | SD | 2/3/2013 07:10 ET | James Healy | City of Venice-Eastside WRF | Pinhole leak developed in 16" forcemain at bell restraint. 325 gallons spilled and entered storm box that connects to Hatchett Creek. Sump installed to return spill to LS. Forcemain repaired. Area limed. | 200 N. Warfield Ave, Venice | pump & lime |  |  | 325 | break-in-line |  | Hatchett Creek | City of Venice-Eastside WRF
| 2013-02-07 | 230p | Lee | SD | 2/7/2013 12:00 ET | Rich Sims | Fort Myers Beach WWTP | Leak at ARV caused approx 100 gallons of reuse water to spill and soak into ground. Disinfected with lime. | 19111 Summerline Rd, Fort Myers | lime |  |  | 100 | break-in-line |  |  | Lee County Utilities
708 | 2013-02-08 | 1102a | Lee | SD | 2/8/2013 11:02 ET | Andy Koebel | Bonita Springs Utilities | Caller reports a wastewater spill from privately owned collections station. Locals noticed a wet area and odor, then reported incident to Bonita Springs Utilities. Upon arriving on scene responders noted that station has had no power and may have had no power for an unknown amount of time. Responders also found a crack in a gravity line with wastewater coming out of it with no estimate as to how much or how long this leak has been occurring. They were able to stop the leak and pump out remaining waste in the station and then spread lime. | 28090 Quails Nest Lane, Bonita Springs | pump & lime |  |  | unknown | break-in-line |  |  | Bonita Springs Utilities
945 | 2013-02-19 | 1026a | Lee | SD | 2/18/2013 09:00 ET | Robert Moulten | City of Ft. Myers Utilities | Caller reports a release of approximately 1000 gallons of untreated wastewater due to a lift station outage in Ft. Myers. Cleanup actions have been taken at the lift station. Surface waters have been affected. | Intersection of Queen Palm Lane and Washingtionia Palm Way, Ft. Myers | HTH |  |  | 1000 | equipment |  |  | City of Ft. Myers Utilities
| 2013-02-19 | 1245p | Lee | SD | 2/19/2013 09:30 ET | Jerry May | Bonita Springs West WRF | 50 gallons overflowed from manhole due to LS malfunction. LS repaired and back online, spill cleaned up and limed. | 26371 Hickory Blvd, Bonita Springs | lime |  |  | 50 | equipment |  |  | Bonita Springs Utilities
970 | 2013-02-20 | 1042a | Sarasota | SWD | 2/20/2013 09:42 ET | Bob Hogan | Sarasota County Utilities | Caller reports that a pump came loose causing a pressure force main to break overflowing a residential septic tank. Between 2,000 and 4,000 gallons of untreated wastewater was released into storm drain located in front of the residence that leads to a small retention pond. Pump truck returning wastewater from storm drain back into the sewage system. | 1208 Vermeer, Nokomis | Vac back into system |  |  | 4000 | equipment |  |  | Sarasota County Utilities
| 2013-02-20 | 420p | Sarasota | SD | 2/19/2013 16:50 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 25 gallons spilled from cleanout on lateral. Lateral repaired, area washed down, vacuumed, and treated with lime. | 1859 Hillview St, Sarasota | lime |  |  | 25 | break-in-line |  |  | City of Sarasota AWWTF
1043 | 2013-02-23 | 437p | Collier | SD | 2/23/2013 14:00 ET | Kevin Rudy | Collier County-South | Collier County Wastewater reports a reclaimed water release in Naples. 300,000 gallons released into a grassy area due to a broken pipe. No clean-up actions required. Repairs completed. No surface waters impacted. | US 41 & Thomasson Dr, Naples | none |  | reclaimed | 300000 | break-in-line |  |  | Collier County Utilities
| 2013-02-25 | 105p | Sarasota | SD | 2/25/2013 10:45 ET | James Healy | City of Venice-Eastside WRF | Approx 10 gallons discharged from top vent of ARV due to malfunction. Discharge vacuumed up and disinfected with lime. | Riveira St & Sovrano St, Venice | vac & lime |  |  | 10 | equipment | 10 |  | City of Venice-Eastside WRF
| 2013-02-26 | 830a | Lee | SD | 2/25/2013 14:00 ET | Jerry May | Bonita Springs West WRF | Approx 20 gallons discharged due to leak in ARV resulting from rust. New ARV installed, spill cleaned and limed. | Imperial Pkwy, Bonita Springs | lime |  |  | 20 | break-in-line |  |  | Bonita Springs Utilities
| 2013-02-26 | 230p | Lee | SD | 2/26/2013 07:30 ET | Cliff Morris | Bonita Springs East WRF | Wash water for fine screening system overflowed into dumpster area due to tripped fuse. Changed out overloads and heaters, disinfected with lime. | 25500 Wellfield Rd, Bonita Springs | lime |  |  | 300 | equipment |  |  | Bonita Springs Utilities
1196 | 2013-02-27 | 228p | Monroe | SD | 2/27/2013 13:30 ET | Michael Martinez | OMI | OMI reports a Wastewater Release in Key West. Less than 500 gallons of raw sewage released from an Air Release Valve line due to maintenance works being performed. Vac-truck was on scene and collected the entire release. No storm drains or surface waters impacted. Caller requests Call-Back from DEP OER. | North Roosevelt Blvd & 7th Street, Key West | vac |  |  | 500 | equipment | 500 |  | OMI
1209 | 2013-02-28 | 931a | Collier | SD | 2/28/2013 07:00 ET | Bart Bradshaw | Marco Island Utilities | City of Marco Island reports a Wastewater Release into the Cottonwood Waterway in Collier County. An unknown amount of raw sewage released from an Air Release Valve due to a malfunctioning valve. Repairs are completed and Clean-up actions are underway. | 1110 San Marco Road, Marco Island | lime |  |  | unknown | equipment |  | Cottonwood Waterway | City of Marco Island | samples taken | FLA014167
1311 | 2013-03-04 | 643p | Glades | SD | 3/4/2013 18:43 ET | Alfonzie Brown | Glades County WWTP | Approx 2000 gallons spilled due to leak in 8" PVD effluent forcemain near manmade wetlands. Switched flow from wetlands to onsite disposal pond. Spill area limed. Contractor to make repairs to forcemain. | Highway 78, Moore Haven | lime |  | treated | 2000 | break-in-line |  |  | City-County PWA | [6 empty] | revised to 2000 gal
| 2013-03-04 | 215p | Lee | SD | 3/3/2013 14:40 ET | Rich Sims | Lee County Utilities | 100 gallons seeped from 2 manholes due to tripped breaker at LS 1100. Power restored and affected area cleaned. Samples requested by association. | 15250 Sonoma Dr, Fort Myers | vac |  |  | 100 | equipment |  |  | Lee County Utilities
1332 | 2013-03-06 | 753a | Sarasota | SD | 3/5/2013 20:20 ET | Jim Petrosky | City of Venice Eastside WRF | City of Venice reports a Wastewater Release in North Venice. 19,000 gallons of reclaimed water released due to a broken 4-inch pipe. No storm drains or surface waters impacted. No clean-up actions required. | 3510 Laurel Road, North Venice | none |  | reclaimed | 19000 | onsite |  |  | City of Venice Eastside WRF
| 2013-03-08 | 800a | Sarasota | SD | 3/6/2013 10:30 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 800 gallons of MLSS spilled when a valve did not fully seat during construction to replace old piping at nitrification basin. Contained onsite, affected area treated with lime. Washed down and vacuumed. | 1850 12th St, Sarasota | lime |  | Patrially Treated | 800 | onsite | 600 |  | City of Sarasota AWWTF
| 2013-03-12 | 248p | Collier | SD | 3/11/2013 13:00 ET | Frank Clark | Marco Island Utilities | Approx 20 gallons leaked from small hole in 6" forcemain. Repairs made and lime spread. | 1002 Royal Marco Way, Marco Island | lime |  |  | 20 | break-in-line |  |  | Marco Island Utilities
| 2013-03-12 | 955p | Sarasota | SD | 3/12/2013. | Jason Brown | Sarasota County Utilities | 200 gallons of sewage bubbled up from sewer main onto the ground. LS shutdown, spill contained and vacuumed, line repaired. Affected area limed. | 381 Yacht Harbor Dr, Sarasota | vac & lime |  |  | 200 | break-in-line | 200 |  | Sarasota County Utilities
| 2013-03-13 | 300p | Collier | SD | 3/13/2013 15:00 ET | John Short | Immokalee Water and Sewer District | Approx 2000 gallons spilled from pipe (used for hauling) from Digester #2 into a new manhole right next to digester. Plugged pipe, pumped back to plant, area limed. | 140 White Way, Immokalee | lime |  |  | 2000 | on-site |  |  | City of Immokalee
| 2013-03-15 | 1100a | DeSoto | SD | 3/15/2013. | Barbara Zvonchenko | US Water-Toby's RV Park | Operator found leak in cap on abandoned pipe coming from CCC. 20 gallons of effluent spilled onto parking lot. Cap to be replaced by site maintainence crew. | WWTP |  |  | treated | 20 | break-in-line |  |  | ELS
| 2013-03-15 | 915a | Sarasota | SD | 3/14/2013 11:45 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 500 gals spilled from manhole onto curb and into stormdrain/pond due to power loss at LS. Power restored, area washed and vacuumed, lime applied. Samples taken at stormwater pond. All samples below limit by 4/3/13. | 1642 12th St, Sarasota | vac & lime |  |  | 500 | equipment | 350 | stormwater pond | City of Sarasota AWWTF
| 2013-03-15 | 115p | Sarasota | SD | 3/15/2013 11:30 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 25 gals seeped from manhole due to grease blockage in main line. Washed, vacuumed, and limed. | East Ave & Princeton St, Sarasota | vac & lime |  |  | 25 | FOG |  |  | City of Sarasota AWWTF
| 2013-03-15 | 350p | Lee | SD | 3/15/2013 15:20 ET | Richard Moulton | City of Fort Myers Central | 800 gals spilled from multiple manholes due to blown fuse at main panel at LS #4. Fuse replaced, spill area treated with HTH and lime. | Cranford Ave & Palm Beach Blvd, Fort Myers | HTH & lime |  |  | 800 | power |  |  | City of Fort Myers Central
| 2013-03-15 | 1155a | Collier | SD | 3/15/2013. | Jim Gammell | Collier County Collections | 20 gallons spilled due to pump blockage during maintenance at Master LS. Cleaned and disinfected with lime. | 312 Harwitch Dr, Naples | lime |  |  | 20 | contractor |  |  | Collier County Collections
| 2013-03-15 | 829p | Sarasota | SD | 3/15/2013. | Jason Brown | Sarasota County Utilities | 4" forcemain break resulted in approx 500 gallons spilled. All recovered. | 1622 Clower Creek Rd, Sarasota |  |  |  | 500 | break-in-line | 500 |  | Sarasota County Utilities
| 2013-03-16 | 1230p | Collier | SD | 3/16/2013 07:00 ET | Frank Clark | Marco Island Utilities | Repair band on 6" forcemain was leaking causing 12,000 gallons to spill onto ground. Vacuumed from retention area, repaired line, and disinfected with lime. | Royal Marco Way & Hideaway Circle, Marco Island | vac & lime |  |  | 12000 | break-in-line | 12000 |  | Marco Island Utilities
1575 | 2013-03-18 | 131p | Collier | SD | 3/18/2013 13:31 ET | Danette Kinaszczuk | Collier County Public Utilities | Caller reports a release of 5,000 gallons of treated effluent in Naples. No clean up actions are needed. | 6671 Glen Harbor Way City, Naples | none |  | treated | 5000 | equipment |  |  | Collier County Public Utilities
| 2013-03-18 | 300p | Collier | SD | 3/15/2013. | Barbara Griffith | Severen Trent-Sabal Palms Elementary | Drainfield cleanout broken by lanscape crew. Unknown amount of treated effluent released onto drainfield. Clean out has been repaired. | 4095 18th Ave NE, Naples | none |  |  | unknown | accident |  |  | Severn Trent
1599 | 2013-03-19 | 306p | Sarasota | SD | 3/19/2013 15:06 ET | Mikey Healy | City of Venice Utilities | Caller reports a release of 50,000 gallons of reclaimed water in Venice. There are no clean up actions needed. | Glen Eagles Drive, Venice | none |  | reclaimed | 50000 | break-in-line |  |  | City of Venice Utilities
1609 | 2013-03-20 | 809a | Lee | SD | 3/19/2013 13:00 ET | Rich Sims | Fiesta Village WWTP | Lee County Utilities reports a Wastewater Release in Fort Myers. 1,000 gallons of raw sewage released from a hole in the Force Main. A nearby storm drain was impacted, but no surface waters were affected. Repairs and clean-up actions complete. | Cypress Lake Drive & South Point Blvd, Fort Myers | vac/lime |  |  | 1000 | break-in-line | 600-700 |  | Lee County Utilities
1615 | 2013-03-20 | 206p | Lee | SD | 3/20/2013 13:15 ET | Lina Quintero | US Water-Lehigh Acres WWTP | Caller reports that an ARV release valve was struck by a vehicle, roughly 1,000 gallons of raw sewage was released into a storm drain on Lee Blvd that leads to an unknown source. No other surface or drinking water was affected. Workers are currently on scene to fix the ARV and isolate the spill. | Sunniland Blvd & Lee Blvd, Lehigh Acres | unknown |  |  | 1000 | accident |  |  | US Water
| 2013-03-21 | 430p | Sarasota | SD | 3/21/2013 09:30 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 100 gallons spilled from manhole due to grease blockage in mainline. Stoppage cleared, spill contained in catch basin and recovered by vac truck. Affected area limed. | North Orange Ave & 17th St, Sarasota | vac & lime |  |  | 100 | FOG | 100 |  | City of Sarasota AWWTF
| 2013-03-22 | 915a | Collier | SD | 3/22/2013 07:00 ET | Justin Frederiksen | City of Naples WWTRF | Less than 1,000 gallons spilled due to ARV housing failure at LS #49. LS shut down, ARV repaired, vac truck cleaned stormwater swale, chlorine sprayed on affected area, LS restarted. | Broad Ave & 8th St South, Naples | vac & chlorine |  |  | < 1,000 | equipment | < 1,000 | stormwater swale | City of Naples WWTRF
1695 | 2013-03-23 | 347p | Lee | SD | 3/23/2013 07:00 ET | Jason Goodrich | City of Sanibel-Donax WRF | A representative with the City of Sanibel reported that approximately 65,000 gallons on untreated domestic wastewater was spilled due to a voltage surge at a lift station. No waterways were affected. Caller advised that lime was placed on the affected area. Lift station bypassed until repairs can be completed. | Sanibel Captiva Rd & Rabbit Rd, Sanibel | lime |  |  | 65000 | power |  |  | City of Sanibel-Donax WRF
| 2013-03-25 | 800a | Highlands | SD | 3/23/2013 19:00 ET | Dan Stroup | City of Sebring WWTF | Electric wire to PLC burned through resulting in pump failure. Less than 1,000 gallons spilled from lift station and manhole. Telemetry failed to send high level alarm as it is also part of PLC unit. Wiring repaired, spill site cleaned and limed. | Sparta Rd and US 27 S, Sebring | lime |  |  | < 1,000 | equipment |  |  | City of Sebring WWTF
1782 | 2013-03-25 | 1136a | Charlotte | SD | 3/25/2013 11:36 ET | Steve Bozman | Charlotte County Utilities | Charlotte County Utilities reported a reclaimed water release of approx 85,500 gallons from an irrigation system. No clean up actions. | 15555 Eagle St, Port Charlotte | none |  | reclaimed | 85500 | equipment |  |  | Charlotte County Utilities |  | Port Charlotte Utility
| 2013-03-27 | 257p | Lee | SD | 3/26/2013 01:00 ET | Richard W. Retz | Aqua Utilities-South Seas WWTP | Approx 200 gallons spilled due to electrical malfunction at lift station. Contractor repaired LS, vac truck hauled sewage, lime applied. | 5400 Plantation Road, Captiva | vac & lime |  |  | 200 | equipment |  |  | Aqua Utilities-South Seas WWTP
1850 | 2013-03-28 | 548a | Sarasota | SD | 3/28/2013 05:15 ET | Bob Seibel | Sarasota County Utilities-Central County WRF | Around 10,000 gallons of treated wastewater spilled on-site at a facility in Sarasota. A UPS (uninterruptible power supply) system overloaded and exploded damaging a PLC (Programmable Logic Controller) unit. This caused an overflow of the system. No clean-up actions required. | 7905 South Macintosh, Sarasota | none |  | treated | 10000 | onsite |  |  | Sarasota County Utilities-Central County WRF
| 2013-03-30 | 1200p | Lee | SD | 3/29/2013. | Melisa Rotteveel | US Water-South Seas WWTF | Less than 5 gallons spilled from clean out near LS #9. Main breaker tripped at LS causing backup in collection system. Reset main breaker and restored power. | LS #9 | unknown |  |  | < 5 | power |  |  | US Water-South Seas WWTF
| 2013-04-02 | 145p | Charlotte | SD | 4/01/2013. | Melisa Rotteveel | US Water-Pelican Harbor | Repairs at lift station caused hydraulic surge through the plant resulting in solids loss from clairifer to ponds. Digester also overflowed onto ground. Estimated 100 gals from clairifer and 50 from digester. Pumps repaired, affected area limed and cleaned, vac truck scheduled to clean solids from CCC. | Pelican Harbor WWTP | lime |  |  | 150 | onsite |  |  | US Water-Pelican Harbor
1971 | 2013-04-03 | 911a | Sarasota | SD | 4/2/2013 08:30 ET | Steve Bothast | Sarasota County Utilities-Central County WRF | Caller reports roughly 36,000 gallons of raw sewage was released from a broken pipe leading from a force main in an abandoned golf course. The leak was located in an abandoned golf course on Draw Street in Sarasota. The sewage did reach a storm drain that led to a retention pond where Sarasota County was able to reclaim the spill. No surface or drinking water was affected. | 5710 Draw Lane, Sarasota | vac & lime |  |  | 36000 | break-in-line | 36000 |  | Sarasota County Utilities-Central County WRF
| 2013-04-03 | 1017a | Lee | SD | 4/3/2013. | David Vallandingham | City of Cape Coral | Rock sitting on 4" reuse line pierced a hole in line causing 200 gallons of reclaimed water to spill. Line repaired. | 2318 SW 4th Ct, Cape Coral | none |  | reclaimed | 200 | break-in-line |  |  | City of Cape Coral
| 2013-04-03 | 1017a | Lee | SD | 4/3/2013. | David Vallandingham | City of Cape Coral | Rock sitting on 4" reuse line pierced a hole in line causing 600 gallons of reclaimed water to spill. Line repaired. | 924 SW 54th Ln, Cape Coral | none |  | reclaimed | 600 | break-in-line |  |  | City of Cape Coral
| 2013-04-03 | 1100a | Highlands | SD | 4/3/2013 10:50 ET | Jim Bedingfield | City of Avon Park | 45 gallons spilled at headworks due to tripped breaker and blocked screen. Reset breaker, disinfected area with lime. | 2504 US 27 South, Avon Park | lime |  |  | 45 | onsite |  |  | City of Avon Park
| 2013-04-05 | 214p | Sarasota | SD | 4/5/2013 09:20 ET | Mickey Healy | City of Venice-Eastside WRF | Less than 500 gals of reclaimed water spilled when ARV saddle was replaced. Water discharged to exvacation and pumped into reuse water pond. Saddle replacement completed. | Glen Eagles Drive, Venice | none |  | reclaimed | 500 | repair |  |  | City of Venice-Eastside WRF
| 2013-04-11 | 1055a | Monroe | SD | 4/10/2013. | Melisa Rotteveel | US Water-Mile Marker 88 Restaurant | Less than 1000 gallons spilled from supernatant tube when line broke during the process of unclogging it. Sludge and wastewater spilled onto ground and parking lot. Vac truck cleaned spill. Affected area limed. Supernatant tube replaced. | Mile Marker 88 Restaurant | vac & lime |  | partially treated | < 1,000 | onsite |  |  | US Water-Mile Marker 88 Restaurant
| 2013-04-11 | 1015a | Lee | SD | 4/11/2013. | Rich Sims | Fort Myers Beach WWTP | 400 gallons of raw spilled onto ground from LS due to pump failure. 1 pump out of service, other pump clogged, computer did not receive alarm page. Computer repaired, 300 gallons removed by vac truck, pump unclogged, area limed. | 17279 San Carlos Dr, Fort Myers | vac & lime |  |  | 400 | equipment | 300 gals |  | Lee County Utilities
| 2013-04-12 | 945a | Sarasota | SD | 4/11/2013 10:30 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 50 pounds of aeration basin grit spilledon roadway from dump truck. Tailgate latch opened when truck went over a speed bump on the way to landfill. Grit picked up, area washed down and limed. | Knights Tr & Laurel Oak Rd, Sarasota | lime |  | grit | 50 lbs | hauling | 50 lbs |  | City of Sarasota
| 2013-04-12 | 822a | Lee | SD | 4/10/2013 14:00 ET | Richard Moulton | City of Fort Myers Central | 350 gallons overflowed from manhole due to high level at LS #44 during force main flow direction exercise. Spill cleaned with vac truck and HTH. | 2100 Rockfill Rd, Fort Myers | vac & HTH |  |  | 350 | overflow | 200 gals |  | City of Fort Myers
| 2013-04-16 | 500p | Sarasota | SD | 4/15/2013 20:52 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 40 gallons seeped out from manhole due to grease blockage in mainline. Area washed down, excess water vacuumed up, and limed. | 3176 Aspinwall St, Sarasota | vac & lime |  |  | 40 | FOG | 40 gals |  | City of Sarasota
| 2013-04-17 | 200p | Lee | SD | 4/15/2013. | Rich Sims | Lee County Utilities | 400 gallons overflowed from manhole due to line blockage caused by roots. Roots removed, spill vacuumed and limed. | 13509 Harbour Ridge Dr, Fort Myers | vac & lime |  |  | 400 | blockage | 300 |  | Lee County Utilities
| 2013-04-17 | 1100a | Sarasota | SD | 4/16/2013 17:00 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 50 gals spilled when contractor was pumping flowable fill grout into old force main line and pressure blew a hole in pipe. Spill contained, washed, vacuumed, and limed. | 246 Morningside Dr, Sarasota | vac & lime |  |  | 50 | contractor | 45 gals |  | City of Sarasota
| 2013-04-19 | 800a | Sarasota | SD | 4/18/2013 15:00 ET | Dave Abene | City of Venice Eastside WRF | 10 gallons of reclaimed water spilled onto grass due to line break. Line was repaired. | 441 Arbor View Ln, Venice | none |  | reclaimed | 10 | break-in-line |  |  | City of Venice
| 2013-04-19 | 400p | Charlotte | SD | 4/19/2013. | Patrick L Godwin | Sandalhaven WWTP | 10 and 20 gallons leaked from 2 manholes when main breaker tripped on LS #6. Reset breaker and disinfected area with chlorine. | 6600 Gasparilla Pines Blvd, Englewood | chlorine |  |  | 30 | power |  |  | Utilities Inc
2414 | 2013-04-23 | 958a | Collier | SD | 4/22/2013 10:30 ET | Robert | South County Wastewater Plant Collier | Caller reports 20 gallons of a mixture of reuse water and 12% Chlorine Solution were released inside of South County Wastewater Facility due to a coupling failure in Naples. No cleanup actions necessary. | 5600 Warren Street, Naples | none |  | reuse/chlorine solution | 20 | onsite |  |  | South County Wastewater Plant Collier
| 2013-04-24 | 355p | Sarasota | SD | 4/24/2013 09:45 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 1 gal spilled from manhole due to blockage in mainline. Washed down, vacuumed, and limed. Blockage cleared. | 2976 Louise St, Sarasota | vac & lime |  |  | 1 | blockage | 1 gal |  | City of Sarasota
| 2013-04-25 | 1153a | Charlotte | SD | 4/25/2013. | Scott Sebor | Knight Island WWTP | RAS line over stilling well missing upon arrival at plant. Shut plant down, repaired line, cleaned and limed spill. Estimated <100 gallons spilled. | Knight Island WWTP | lime |  |  | 100 | unknown |  |  | Knight Island Utilities
| 2013-04-26 | 1145a | Sarasota | SD | 4/26/2013. | Rick Newkirk | North Port Utilities | Approx 50 gallons spilled into containment ditch due to broken ARV. ARV removed, area washed down, vacuumed and limed. | 3184 Sumter Blvd, North Port | vac & lime |  |  | 50 | break-in-line |  |  | North Port Utilities
2533 | 2013-04-28 | 652p | Collier | SD | 4/28/2013 18:40 ET | Raymond See | Collier County-North | Caller reports a release of 1,500 gallons of reclaimed water in Naples. No storm water systems and no surface waters were affected. No clean up actions were taken. | 1294 Grand Isle Court, Naples | none |  | reclaimed | 1500 | break-in-line |  |  | Collier County Utilities
| 2013-04-29 | 721p | Sarasota | SD | 4/29/2013. | Jason Brown | Sarasota County Utilities | Approx 200 gallons overflowed from manhole due to blockage in line. Line flushed, affected area vacuumed and limed. | 2112 Muskogee Tr, Nokomis | vac & lime |  |  | 200 | blockage |  |  | Sarasota County Utilities
| 2013-04-30 | 1100a | Sarasota | SD | 4/30/2013. | Robert Clark | City of Venice | Approx 10 gallons spilled from clean-out due to momentary blockage. Blockage cleared, line jetted, area limed. | 200 N Warfield Ave, Venice | lime |  |  | 10 | blockage |  |  | City of Venice Utilities
| 2013-05-02 | 515p | Lee | SD | 5/2/2013 15:00 ET | Lina Quintero | US Water-Lehigh Acres WWTP | Approx 800 gals spilled when ARV was hit by car. Affected area limed. | 4300 Lee Blvd, Lehigh Acres | lime |  |  | 800 | accident |  |  | US Water
| 2013-05-02 | 325p | Collier | SD | 5/2/2013 12:30 ET | Jim Gammell | Collier County Collections | 30 gals spilled as a result of tranducer failure due to grease/debris. Transducer failed to turn on bypass pump. Station bypassed til repairs can be completed. Area cleaned and limed. | Piper Blvd, Palm River | vac & lime |  |  | 30 | equipment | 30 gals |  | Collier County Utilities
| 2013-05-08 | 1120a | Collier | SD | 5/8/2013 10:30 ET | Jesse Komorny | Collier County Collections | 100 gals spilled due to leaky ARV. ARV repaired, affected area vacummed and limed. | Davis Blvd & Cedar Hammock Cir, Naples | vac & lime |  |  | 100 | break-in-line | 50 |  | Collier County Utilities
2871 | 2013-05-09 | 608p | Highlands | SD | 4/25/2013 18:08 ET | Betty |  | Caller reports that raw sewage is being dumped into a lake behind her residence in Sebring from an unknown origin. The caller also states that this has been going on for couple weeks. | 615 Memorial Drive, Sebring | none |  |  | unknown | break-in-line |  | Lake Sebring | Whisper Lake MHP
| 2013-05-10 | 900a | Highlands | SD | 5/10/2013. | Dan Stroup | City of Sebring | Unknown amount spilled due to force main break. Spill may have entered Lake Sebring. City of Sebring notified responsible party and assisted them with locating contractor for repairs. | 619 Memorial Dr, Sebring | unknown |  |  | unknown | break-in-line |  | Lake Sebring | Whisper Lake MHP
| 2013-05-11 | 600p | Lee | SD | 5/11/2013 07:30 ET | Burke Young | Bonita Springs West WRF | 600 gallons spilled from LS after both pumps tripped. Area vacuumed and limed. | 2281 Fountain Lakes Blvd, Bonita Springs | vac & lime |  |  | 600 | equipment | 150 gal |  | Bonita Springs Utilities
| 2013-05-15 | 230p | Desoto | SD | 5/15/2013 14:30 ET | Alex Shannon | Desoto County Regional WWTF | 400 gals spilled due from leak at force main joint caused by oak tree removal. Joint replaced, area limed. | US 17, Arcadia | lime |  |  | 400 | break-in-line |  |  | Desoto County Utilities
| 2013-05-15 | 200p | Highlands | SD | 5/15/2013 10:00 ET | Dan Stroup | City of Sebring WWTF | Less than 1000 gals spilled when glued 90 on force main at Fernway LS seperated. Line repaired, area vacuumed and limed. | Fernway Ave, Sebring | vac & lime |  |  | <1000 | break-in-line | 400 gals |  | City of Sebring
3003 | 2013-05-16 | 947a | Collier | SD | 5/16/2013 09:00 ET | Danette Kinaszczuk | Collier County-South | Collier County Public Utilities reports a reclaimed water release in Naples. 1,000 gallons of Irrigation-grade Reclaim Water released from a private line. No clean-up actions required. | 7848 Classics Drive, Naples | none |  | reclaimed | 1000 | break-in-line |  |  | Collier County Utilities
3022 | 2013-05-17 | 1053a | Collier | SD | 5/17/2013 10:53 ET | Danette Kinaszczuk | Collier County-South | Collier County Public Utilities reports a Treated Reclaim Water Release in Naples. 5,000 gallons of irrigation grade water released due to a break in a 2-inch private line. No clean-up actions required. | 1121 East Tamiami Tr, Naples | none |  | reclaimed | 5000 | break-in-line |  |  | Collier County Utilities
| 2013-05-17 | 202p | Collier | SD | 5/16/2013 16:30 ET | Danette Kinaszczuk | Collier County-North | 500 gals reclaimed water released in Pelican Bay Services GST #2 due to overflow. Reclaimed water absorbed into surrounding grassy area. | Pelican Bay Services GST #2, Naples | none |  | reclaimed | 500 | overflow |  |  | Collier County Utilities
| 2013-05-20 | 730a | Lee | SD | 5/19/2013 12:00 ET | Jerry May | Bonita Springs West WRF | 2in PVC nipple attached to ARV below ground was defective allowing approx 200 gals to spill. 2in nipple replaced, area limed. | 26967 Lost Woods Cir, Bonita Springs | lime |  |  | 200 | break-in-line |  |  | Bonita Springs Utilities
| 2013-05-20 | 230p | Collier | SD | 5/20/2013 12:00 ET | Frank Clark | Marco Island Utilities | End cap broke off of 4" force main causing 60 gals to spill onto ground. Line repaired, area limed. | 915 Palm Point Dr, Goodland | lime |  |  | 60 | break-in-line |  |  | Marco Island Utilities
3128 | 2013-05-21 | 247p | Collier | SD | 5/21/2013 14:47 ET | Steve Nagy | Collier County Collections | Caller reports a release of 2,500 gallons of wastewater released to the ground in Naples when car hit ARV. Clean up actions were taken. No storm water systems and no surface waters were affected. | 9950 Goodlette Frank Rd, Naples | lime |  |  | 2500 | accident |  |  | Collier County Utilities
| 2013-05-21 | 745a | Lee | SD | 5/20/2013 17:10 ET | Jerry May | Bonita Springs West WRF | Transfer switch malfunctioned during power outage causing 700 gals to spill from LS #241 onto ground. Switch problem was investigated/repaired/tested, area was limed. | 27758 Arroyal St, Bonita Springs | lime |  |  | 700 | power |  |  | Bonita Springs Utilities
3210 | 2013-05-25 | 103a | Collier | SD | 5/25/2013 17:00 ET | Jon Pratt | Collier County-North | 30,000 gallons of treated wastewater spilled on-site at a facility in the Naples area due to a ruptured line. The water was pumped back into the system. Clean-up/recovery actions complete. No off-site impact reported. | 10500 Goodlette Rd, Naples | lime |  | treated effluent | 30000 | onsite | 30000 gal |  | Collier County Utilities
| 2013-05-26 | 434p | Monroe | SD | 5/26/2013 10:00 ET | Melisa Rotteveel | US Water-Chesapeake Beach Resort | Clog in transfer line from still well to lift station caused approx 500 gals to be discharged onto surrounding ground near tennis court. Area treated with chlorine. | Chesapeake Beach Resort | chlorine |  |  | 500 | blockage |  |  | US Water
3247 | 2013-05-27 | 113p | Lee | SD | 5/27/2013 06:57 ET | Patti DiPiero | Fort Myers Beach WWTP | Caller is reporting a wastewater spill of 50,000 gallons in Ft. Myers. Caller stated that the spill has ceased and the wastewater contained to a storm culvert. Testing is underway to determine how far the wastewater went. The utility does not believe it entered surface water. | Pine Ridge Rd & Gulf Reflections Dr, Ft. Myers | vac & lime |  |  | 50000 | break-in-line | 40,000 gal | storm culvert | Lee County Utilities |  | FLA144215
3280 | 2013-05-29 | 945a | Lee | SD | 5/28/2013 23:30 ET | Lina Quintero | US Water-Del Prado WWTP | Caller is reporting a treated effluent spill in North Ft. Myers. Caller stated that the spill was 100,000 gallons. No clean up actions are needed. | 3410 Clubview Dr, North Ft. Myers | none |  | reclaimed | 100000 | break-in-line |  |  | US Water
3281 | 2013-05-29 | 949a | Lee | SD | 5/28/2013 23:30 ET | Lina Quintero | US Water-Del Prado WWTP | Caller is reporting a 400,000 gallon treated effluent spill in North Ft. Myers. Caller stated that the spill entered a nearby creek and there is planned testing. UPDATE: all fecal test results came back below limits. | Laurel Rd & Dorlee Ln, North Ft. Myers | unknown |  | reclaimed | 400000 | break-in-line |  | Powel Creek | US Water
3320 | 2013-05-30 | 715p | Collier | SD | 5/30/2013 19:15 ET | Jim Gammell | Collier County-North | Caller reports a relcaimed water release of approximately 2,000 gallons from an irrigation line in Naples. The leak has been stopped but some of the water did reach a storm drain that entered an unknown lake inside of the Pelican Bay community. | 6040 Ridgewood Drive, Naples | none |  | reclaimed | 2000 | break-in-line |  |  | Collier County Utilities
| 2013-05-30 | 150p | Collier | SD | 5/29/2013 14:15 ET | Danette Kinaszczuk | Collier County-South | 900 gals reclaimed water released on private side of line. Absorbed into surronding grassy/stormwater areas. | 7457 Matinique Ter, Naples | none |  | reclaimed | 900 | break-in-line |  |  | Collier County Utilities
3324 | 2013-05-31 | 902a | Sarasota | SD | 5/30/2013 11:00 ET | Bill McKee | Aqua Utilities | A representative with Aqua Utilities advised that approximately 2,500 gallons of wastewater was spilled in Sarasota due to a soft start failure at a lift station. No waterways were affected. The affected area was vacuumed and covered with lime. | 2500 Martin Luther King Blvd. Sarasota | vac/lime |  |  | 2500 | negligence |  |  | Aqua Utilities
3382 | 2013-06-03 | 1144 | Lee | SD | 6/3/2013 11:44 ET | Lina Quintero | US Water-Lehigh Acres WWTP | 4000 Gallon wastewater release in 504 E 3th St in Lehigh Acres due to crack in 4" asbestos cement sewer line. The release has ceased and clean-up actions are underway. | 504 E 3th St, Lehigh Acres | vac & lime |  |  | 4000 | break-in-line | 500 gals |  | US Water
| 2013-06-03 | 1030a | Highlands | SD | 6/2/2013. | Lisa Holmes | Pugh Utilities-Francis I | Clog in digester caused 400 gallons to spill onto ground. Unclogged digester, cleaned and limed affected area. | Francis I WWTP | lime |  | sludge | 400 | on-site |  |  | Francis I MHP
| 2013-06-03 | 130p | Collier | SD | 6/3/2013 12:30 ET | Jim Gammell | Collier County Collections | ARV failed due to debris in check valve causing 200 gals to leak onto ground. ARV repaired, area cleaned and limed. | Bridgewater Bay Blvd & Twilight Ln, Naples | lime |  |  | 200 | break-in-line |  |  | Collier County Utilities
3416 | 2013-06-04 | 208p | Collier | SD | 6/4/2013 13:30 ET | Rob Kain | Collier County-North | Collier County Public Works is reporting a 48,000 gallon spill of reclaimed water. The incident happened at 9261 Troon Lakes Dr in Naples when a 4" main private line was damaged. CCPW is not requesting any assistance at this time. | 9261 Troon Lakes Dr, Naples | none |  | reclaimed | 48000 | break-in-line |  |  | Collier County Utilities
| 2013-06-05 |  | Monroe | SD | 6/5/2013. | Melisa Rotteveel | US Water-Waldorf Plaza | RAS piping split apart allowing approx 500 gallons of solids to discharge onto ground. Piping repaired, area cleaned. | Waldorf Plaza WWTP | unknown |  | sludge | 500 | on-site |  |  | US Water
3556 | 2013-06-06 | 532p | Sarasota | SD | 6/6/2013 13:00 ET | Victor Carlano | Sarasota County-CCU WRF | Caller reports 2,000 gallons of raw sewage have been released from a lift station in Sarasota. The cause is currently unknown and the release has not entered any surface water or storm drains. Sarasota County currently has a vacuum truck on scene to clean up the pool as well as plans to lime the incident. UPDATE: Spill occurred when 2 communication cards on PLC rack shorted out. | 7302 Bounty Drive, Sarasota | vac & lime |  |  | 2000 | equipment | 400 gals |  | Sarasota County
3695 | 2013-06-11 | 434p | Collier | SD | 6/11/2013 14:00 ET | Martin | Collier County-North | Collier County Utilities is reporting a Reclaimed Water Release of approximately 3,000 gallons. They stated that no water ways were affected by the spill, and that it went into a grassy field so no clean up actions have been taken. | 101 Palm Dr, Naples | none |  | reclaimed | 3000 | break-in-line |  |  | Collier County Utilities
| 2013-06-11 | 400p | Collier | SD | 6/11/2013 07:15 ET | Jim Gammell | Collier County-North | 150 gallons total spilled from lift station and 10 manholes due to power failure (main FPL underground transmission feeder burned up). Generator hooked up, spill cleaned and limed. | Piper Blvd & Palm View Dr, Sharwood Blvd, Naples | vac & lime |  |  | 150 | power | 150 |  | Collier County Collections
3719 | 2013-06-12 | 1155a | Sarasota | SD | 6/11/2013 13:00 ET | Bill McKee | Aqua Utilities-Fruitville WWTP | Aqua Utilities is reporting a 2500 gallon release of raw sewage due to a force main failure. They have contained the release and clean up actions have been taken. No waterways have been affected by the release. | 1492 Blind Brook, Sarasota | vac & lime |  |  | 2500 | break-in-line |  |  | Aqua Utilities
3760 | 2013-06-13 | 111p | Lee | SD | 6/12/2013 14:00 ET | Rich | Lee County Utilities | Caller reports that 8,000 gallons of treated reuse wastewater was released in Fort Myers due to a contractor excavating without proper locates. | Pine Chase Drive and Three Oaks Parkway, Fort Myers | none |  | reclaimed | 8000 | contractor |  |  | Lee County Utilities
3775 | 2013-06-13 | 953p | Lee | SD | 6/13/2013 21:53 ET | Lina Quintero | US Water-Lehigh Acres WWTP | Caller reports 1,000 gallons of raw sewage being released from a broken force main (possibly from excessive rainwater) in Lehigh Acres. The release is still occurring as US Water Services is attempting to fix the main. Wastewater has entered an unnamed canal that leads to an unknown source. UPDATE: coupling came apart on 10" asbestos cement forcemain. Area cleaned and disinfected. | 37 N Alabama Rd, Lehigh Acres | lime |  |  | 1000 | break-in-line |  |  | US Water Services
| 2013-06-13 | 1230a | Lee | SD | 6/12/2013 13:00 ET | Richard Sims | Lee County Utilities | Contractor (Roberts Drilling) damaged line while boring for irrigation line installation. 800 gallons spilled on ground. Contractor to make repairs. | Ben Hill Griffin & College Club Blvd, Estero | vac |  |  | 800 | contractor | 300 gals |  | Roberts Drilling
| 2013-06-13 | 200p | Lee | SD | 6/13/2013 08:00 ET | Richard Sims | Lee County Utilities | A contractor trying to isolate the reuse system closed valves without permission causing a manhole and cleanout to overflow. Affected area vacuumed and limed. | 18883 Cypress View Dr, Estero | vac & lime |  |  | 600 | contractor | 400 gals |  | ElectriCom
| 2013-06-13 | 344p | Desoto | SD | 6/10/2013. | Scott Sebor | Plantation Restaurant | Operator found lift station alarm on during visits 6/10/13 through 6/12/13 and notified management. LS finally overflowed onto ground on Wednesday, approx 1500 gals. | 4135 SW Highway 17, Arcadia | unknown |  |  | 1500 gals | unknown |  |  | Plantation Restaurant
3781 | 2013-06-14 | 958a | Sarasota | SD | 6/14/2013 09:58 ET | James Healy | City of Venice-Eastside WRF | City of Venice reports a Treated Reclaim Water Release in Venice. 1,200 Gallons have been released due to leaking reuse valve. Crews are en route to conduct repairs. This release may impact a nearby Retention Pond. | Edmonson Rd & Capri Isles Blvd, Venice | none |  | reclaimed | 1200 | break-in-line |  |  | City of Venice
3801 | 2013-06-14 | 628p | Monroe | SD | 6/14/2013 16:45 ET | Zully | City of Marathon | Caller reports that approximately 1,000 gallons of raw sewage was released from a broken force main in Marathon. The release did enter a storm drain but was contained. Material has been placed in the storm drain to prevent the release from spreading as well as a pump truck on scene to clean up the material. | 95 Cocoa Plum Drive Marathon | pumped and recovered |  |  | 1000 | break-in-line |  |  | City of Marathon
3837 | 2013-06-16 | 309p | Charlotte | SD | 6/16/2013 09:00 ET | Charley Rine | East Port WRF | Caller reports a 1,500 gallon release of untreated wastewater in Port Charlotte due to deteriorated joint on 6" force main. No storm water systems and no surface waters were affected. Clean up actions were completed. | 2475 Ambrose Ln, Port Charlotte | vac& lime |  |  | 1500 | break-in-line | <1,000 |  | Charlotte County Utilities
| 2013-06-16 | 1015a | Sarasota | SD | 6/15/2013 10:00 ET | Bill McKee | Aqua Utilities-Fruitville WWTP | 200 gals spilled due to line blockage. Blockage cleared, majority of spill soaked into ground, some reached retention pond. Samples taken. | 5612 Forester Lake Dr, Sarasota | lime |  |  | 200 | blockage |  |  | Aqua Utilities
3849 | 2013-06-17 | 1023a | Monroe | SD | 6/16/2013 19:00 ET | Zurry Hemeyer | City of Marathon | A representative with City of Marathon reported that approximately 1,500 gallons of wastewater was spilled due to a broken pipe. No waterways were affected. The affected area was vacuumed and covered with lime. | 57335 Morton Street Marathon | vac/lime |  |  | 1500 | break-in-line |  |  | City of Marathon
3857 | 2013-06-17 | 1242p | Sarasota | SD | 6/17/2013 12:42 ET | Jason Brown | Sarasota County Utilities | Caller reports a Wastewater release of over 1000 gallons in Nokomis. Surface waters and a storm water systems has been affected. Clean up actions are in progress. | 280 Village Dr, Nokomis | vac |  |  | >1000 | break-in-line |  | canal to Blackburn Bay | Sarasota County Utilities | sampling
3880 | 2013-06-18 | 1146a | Collier | SD | 6/18/2013 11:46 ET | Marty McAndrew | Collier County-South | Caller reports 100,000 Gallon release of treated effluent water discharged in Naples. Address is 4020 Lakewood Blvd 34112. No clean up actions have been taken at this time, discharge was in a grassy area and is believed to have gone down a storm drain. | 4020 Lakewood Blvd, Naples | none |  | reclaimed | 100000 | break-in-line |  | storm drain | Collier County Utilities
| 2013-06-18 | 200p | Charlotte | SD | 6/16/13 10:00 ET | Ed McCampbell | Punta Gorda WWTP | Less than 100 gals spilled near headworks when LS controller failed and pumps wouldn't operate automatically. | 30999 Bermont Rd, Punta Gorda | washed down |  |  | 100 | on-site |  |  | City of Punta Gorda
3907 | 2013-06-19 | 208p | Lee | SD | 6/19/2013 11:41 ET | Rich Sims | City of Fort Myers-South | Lee County Utilities is reporting a spill of 18,000 gallons at the address below. They have contained the spill to a ditch and further clean up actions have been initiated. No storm drains or surface waters have been impacted by this release. Line repaired, spill vacuumed and limed. | 12551 South Cleveland Ave, Fort Myers | vac & lime |  |  | 18000 | break-in-line | 15,000 gal |  | Lee County Utilities
| 2013-06-19 | 338p | Highlands | SD | 6/6/2013 14:15 ET | Jim Bedingfield | City of Avon Park | 250 gals spilled from oxidation ditch while doing clarifier maintenance. Spill disinfected with lime. | City of Avon Park WWTP | lime |  |  | 250 | on-site |  |  | City of Avon Park
| 2013-06-19 | 230p | Sarasota | SD | 6/19/2013 09:30 ET | Dave Abene | City of Venice-Eastside WRF | Break in 3/4" reuse line caused 800 gals of reclaimed water to spill onto nearby grassy area and into stormwater basin. Line repaired. | 1442 Strada D Oro, Venice | none |  | reclaimed | 800 | break-in-line |  |  | City of Venice
| 2013-06-19 | 230p | Sarasota | SD | 6/19/2013 12:30 ET | Dave Abene | City of Venice-Eastside WRF | Break in 1" reuse line caused 100 gals of reclaimed water to spill onto surrounding grassy area. Line repaired. | 1168 Kingston Wy, Venice | none |  | reclaimed | 100 | break-in-line |  |  | City of Venice
| 2013-06-19 | 440p | Lee | SD | 6/18/2013 20:00 ET | Lina Quintero | US Water-Lehigh Acres WWTP | 500 gals spilled due to break in 4" asbestos cement sewer line. Line repaired, area cleaned and limed. | 500 E 3rd St, Lehigh Acres | lime |  |  | 500 | break-in-line |  |  | US Water
| 2013-06-19 | 952a | Sarasota | SD | 6/18/2013 15:00 ET | Bill McKee | Aqua Utilities-Fruitville WWTF | 50 gals spilled from manhole due to blockage in dead end manhole run. Line was jetted, area disinfected with lime. | 1702 Tarpon, Sarasota | lime |  |  | 50 | blockage |  |  | Aqua Utilities
3937 | 2013-06-20 | 317p | Collier | SD | 6/20/2013 13:30 ET | Rob Kaine | Collier County-North | Caller reports 9,600 gallons of reclaim water released from a cut irrigation line in Naples. The water did reach a storm drain that led to an unknown retention pond. | 2200 Bent Tree Ln, Naples | none |  | reclaimed | 9600 | break-in-line |  |  | Collier County Utilities
| 2013-06-20 | 406p | Collier | SD | 6/20/2013. | Jim Gammell | Collier County Collections | 30 gals spilled when contractor bumped abandoned curb stop with backhoe. Spill contained in excavation site and pumped back to LS. Area disinfected with lime. | 6654 Harwich Ct, Glen Eagle | vac & lime |  |  | 30 | contractor | 30 gals |  | Collier County Utilities
4051 | 2013-06-25 | 1112a | Monroe | SD | 6/25/2013 10:15 ET | Daniel Saus | Key Largo WWTF | Key Largo Wastewater Treatment Facility is reporting a wastewater spill in Key Largo. Caller states that a contractor broke a force main spilling over 1,000 gallons of wastewater. Caller stated no waterways or storm drains were affected and the spill is contained. | mm 94.5 US 1, Key Largo | vac/disinfect |  |  | 5000 | contractor | 5,000 gals |  | Key Large Wastewater Treatment District
| 2013-06-26 | 130p | Sarasota | SD | 6/26/2013 13:30 ET | Jason Brown | Sarasota County-BeeRidge WRF | 200 gals spilled due to blockage. Vac truck cleared blockage, 200 gals of raw/storm water vacuumed, area limed. | Baycedar Ln, Sarasota | vac & lime |  |  | 200 | blockage | 200 gals |  | Sarasota County Utilities
| 2013-06-26 | 814a | Highlands | SD | 6/26/2013 06:00 ET | Gary Freeman | Town of Lake Placid-North | 500 gals spilled from LS due to power outage/switch/timer failure. Contained on site, power restored, will install battery back-up emergency call service. | 260 N Main Ave, Lake Placid | unknown |  |  | 500 | power |  |  | Town of Lake Placid
| 2013-06-28 | 900a | Collier | SD | 6/26/2013 09:00 ET | Anthony Milden | Collier County Collections | 30 gals discharged from manhole due to damage/bloackage caused by communications line. Line jetted and repaired, area limed. | 503 Cypress Way East, Naples | lime |  |  | 30 | blockage |  |  | Collier County Utilities
| 2013-07-01 | 1100a | Lee | SD | 6/30/2013 10:00 ET | Lina Quintero | US Water-Lehigh Acres WWTP | Less than 1000 gals spilled due to break in 10" asbestos cement forcemain. Line repaired, area cleaned and limed. | 37 N Alabama Rd, Lehigh Acres | lime |  |  | < 1000 | break-in-line |  |  | US Water
| 2013-07-01 | 1229p | Highlands | SD | 7/1/2013. | Lisa Holmes | Pugh Utilities-Lakeside Village | CCC bypassed and 100 gallons spilled due to heavy rains. Area cleaned and limed. | Lakeside Village MHP WWTP | lime |  |  | 100 | rain |  |  | Lakeside Village MHP
| 2013-07-01 | 950a | Highlands | SD | 7/1/2013 09:15 ET | Lisa Holmes | Pugh Utilities-Tropical Harbor | Over 1000 gallons overflowed from CCC onto ground due to heavy rainfall and infiltration. Solids pushed to ponds. | Tropical Harbor WWTP | unknown |  | partially treated | >1,000 | rain |  |  | Tropical Harbor MHP
4266 | 2013-07-02 | 501p | Charlotte | SD | 7/2/2013 13:00 ET | Charlie Rine | 941-764-4555 | Caller reports 15,000 gallons of raw sewage was released from a force main break in Port Charlotte. Storm water system and surface waters were affected. Clean up actions were taken. | 1515 Forest Nelson Blvd., Port Charlotte | vac/lime |  |  | 15000 | break-in-line | 9000
| 2013-07-02 | 230p | Lee | SD | 7/1/2013 12:00 ET | Rich Sims | City of Fort Myers-South | Pipe structure rotted out causing 200 gallons to spill onto ground. Line replaced, isolation valve added, affected area limed. | 12551 South Cleveland Ave, Fort Myers | lime |  |  | 200 | break-in-line |  |  | City of Fort Myers
| 2013-07-02 | 230p | Lee | SD | 7/1/2013 16:00 ET | Rich Sims | Fiesta Village WWTP | Contractor (Electricom) bored through 6" forcemain causing 150 gals to spill. Line isolated and repaired, area limed. | Cypress Lakes Dr & Broadhurst Lp, Fort Myers | lime |  |  | 150 | contractor |  |  | Electricom
4287 | 2013-07-03 | 1200p | Glades | SD | 7/3/2013 09:00 ET | Al | Calusa Lodge | Caller reports that approximately 800 gallons of treated sludge was released from a wastewater facility in Moore Haven due to a malfunctioning pump. No surface or drinking water was affected by the release. Lime applied, dried sludge raked up. | HWY 78 & Loop Rd, Lakeport | lime |  | mixed liquor | 800 | equipment |  |  | Joe Rowlett
4296 | 2013-07-03 | 224p | Lee | SD | 7/2/2013 12:00 ET | Lina | US Water Services | Per Lina at US Water Services: Due to continuing heavy rainfall in the area, the facility experienced another Treated Effluent Release of 16,900 gallons this morning. Additional overflows may occur as long as heavy rains impact the area. |  | none |  | treated | 16900 | rain
4319 | 2013-07-03 | 1030p | Lee | SD | 7/3/2013 22:11 ET | Andy Koebel | Bonita Springs West WRF | 10,000 gallons of untreated domestic wastewater spilled at in the Bonita Springs area due to a traffic crash that damaged an air release valve. No waterways affected. Clean-up conducted by the responsible party. | Old Business US-41 & Bonita Beach Rd, Bonita Springs | vac & lime |  |  | 10000 | accident | 2000 gals |  | Bonita Springs Utilities
4358 | 2013-07-04 | 613p | Collier | SD | 7/4/2013 17:30 ET | Millie Kelley | Collier County Collections | Caller reports that 1,000+ gallons of raw sewage is being released from a broken pipe in Naples. The release is still active and 15 pump trucks are currently enroute to clean up the spill. One storm drain that has an unknown source has been affected on Saint Andrews Blvd. UPDATE: 205,400 gal spilled. Temp repairs made 7/4, permanent repairs finished 7/9. Samples collected from Lely canal and Santa Barbara sw pond. All results below limits. | Rattlesnake Hammock Rd & Santa Barbara Blvd, Naples | vac & lime |  |  | 205400 | break-in-line | 8000 gals | Lely canal | Collier County Utilties
4368 | 2013-07-05 | 741a | Sarasota | SD | 7/3/2013 07:41 ET | Roger Hostetler | Sarasota County-Siesta Key AWWTP | 1,400 gallons of partially treated wastewater spilled on-site at a facility due to hydraulic overload. No waterways affected. Clean-up conducted by the responsible party. Vacuumed and limed. | 5200 Oakmont Place, Siesta Key | vac & lime |  |  | 1400 | rain | 1000 gals |  | Sarasota County Utilities
4390 | 2013-07-05 | 211p | Lee | SD | 7/5/2013 14:11 ET | Richard Moulton | City of Fort Myers-Central | Caller reports of an ongoing wastewater release occurring in Fort Myers of over 1,000 gallons. The release is coming from an overflowing manhole due to excessive flooding. The wastewater is entering the Caloosahatchee River. | 1215 Alhambra Drive, Fort Myers | HTH |  |  | 1000 | rain |  | Caloosahatchee River | City of Fort Myers
| 2013-07-05 | 140p | Sarasota | SD | 7/4/2013. | Bill McKee | Aqua Utilities-Fruitville WWTF | 500 gallons spilled due to power outage (believed to be caused by lightning storm in area). Spill contained to retention pond. Area limed and samples pulled. All samples under limits by 7/9/13. | 3028 Lockwood Meadows Cir, Sarasota | lime |  |  | 500 | power |  |  | Aqua Utilities
| 2013-07-05 | 922a | Lee | SD | 7/4/2013 09:00 ET | Lina Quintero | US Water-Lehigh Acres WWTP | 500 gals spilled due to break in 10" asbestos cement forcemain. Line isolated, repaired, area cleaned, limed. | 37 N Alabama Rd, Lehigh Acres | lime |  |  | 500 | break-in-line |  |  | US Water
4368 | 2013-07-05 | 932a | Lee | SD | 7/4/2013 21:00 ET | Lina Quintero | US Water-Del Prado WWTP | Corroded/leaking brass nipple on ARV caused 3000 gallons to spill onto ground. Nipple replaced, ball valve installed, area was cleaned. | Pondella Rd & Barrett Rd, North Fort Myers | disinfected |  |  | 3000 | break-in-line | 2000 gals |  | US Water
4439 | 2013-07-06 | 300p | Sarasota | SD | 7/6/2013 15:00 ET | Trisha Nihart | Sarasota County-Siesta Key AWWTP | Caller reports a Wastewater Release in Siesta Key. 99,000 gallons of storm water mixed with partially treated wastewater released from the Siesta Key Wastewater Treatment Plant due to heavy rains impacting the area. The release entered the Grand Canal. | 5200 Oakmont Place, Siesta Key | none |  | partially treated | 99000 | rain |  | Grand Canal | Sarasota County Utilities
4445 | 2013-07-06 | 459p | Collier | SD | 7/6/2013 14:59 ET | Derick Galvan | Immokalee Water & Sewer District | Caller reports an ongoing raw sewage release in Immokale of currently 6,000 gallons. The release occurred from a broken gravity line. The release has not entered any storm drains, surface water, or drinking water. Vacuum trucks are currently on scene | Gross Ave, Immokale | vac |  |  | >6000 | break-in-line |  |  | Immokalee Water & Sewer District
4451 | 2013-07-06 | 759p | Monroe | SD | 7/6/2013 14:30 ET | Julie | City of Marathon | Caller reports a wastewater release of 5,200 gallons of wastewater in Marathon. The release occurred after a contractor struck a force main. The release did not enter any storm systems, surface water, or drinking water. Pump trucks were brought into clean up the release. | 57437 Morton Street, Marathon | pump trucks |  |  | 5200 | contractor |  |  | City of Marathon
4487 | 2013-07-08 | 1217p | Sarasota | SD | 7/8/2013 12:17 ET | Victor Carlano | Sarasota County-Bee Ridge WRF | Caller reports a wastewater release of 10,000 gallons in Sarasota. Internal battery for PLC went bad. A Stormwater system and surface waters were affected. Clean up actions are in progress. Vacuumed, limed, pulled samples, replaced battery. | 7650 Bee Ridge Rd, Sarasota | vac & lime |  |  | 10000 | equipment | 5200 gals |  | Sarasota County
4492 | 2013-07-08 | 241p | Lee | SD | 7/8/2013 10:00 ET | Lina Quintero | US Water-Del Prado WWTP | US Water Services INC is calling to report the release 1,000 gallons of wastewater from a twelve (12) inch force main in North Fort Myers. The release was stopped by 1330. The cause of the release was unknown. No waterways or storm drains were impacted. A Vacuum truck is en-route to collect the released material so that further clean-up and repairs can be conducted. | Prado Boulevard and Power Creek, North Fort Myers | vac and repair |  |  | 1000 | unknown |  |  | US Water Services Inc.
4507 | 2013-07-08 | 714p | Collier | SD | 7/8/2013 16:30 ET | Derick Galvan | Immokalee Water & Sewer District | Caller reports a Wastewater Release of 16,000 gallons in Immokalee. Maintenance personnel forgot to turn good pump back on after checking on bad pump. A storm water system was affected. Clean up actions are in progress. | 12th Street, Immokalee | vac & lime |  |  | 16000 | negligence |  |  | Immokalee Water & Sewer District
| 2013-07-08 | 415p | Sarasota | SD | 7/1/2013 - 7/3/2013. | Roger Hostetler | Sarasota County-Venice Gardens WRF | 420 gallons leaked from under manhole lid due to both pumps running in lift station and back up in gravity line. Cleaned with vac truck. Discharge reached lake system. Samples pulled and all results under limits by 7/8/13. | Willow Ln & Shamrock Blvd, Venice | unknown |  |  | 420 | overflow |  | lake system | Sarasota County Utilities
4526 | 2013-07-09 | 339p | Sarasota | SD | 7/9/2013 15:39 ET | Jason Brown | Sarasota County-Bee Ridge WRF | Caller reports a treated effluent release in Sarasota. Over 1,000 gallons was released. Contactor drilled through reuse main. No clean up actions are needed. | Honore Ave & Clark Rd, Sarasota | none |  | reclaimed | >1000 | contractor |  |  | Sarasota County
| 2013-07-09 | 815a | Charlotte | SD | 7/8/2013. | Melisa Rotteveel | US Water-Pelican Harbor | Perc pond overflow due to heavy rains. Leak discovered between aeration basins. | Pelican Harbor WWTP | unknown |  | partially treated | unknown | rain |  |  | Pelican Harbor
4561 | 2013-07-10 | 521p | Lee | SD | 7/10/2013 17:00 ET | Jason Goodrich | City of Sanibel | Caller is reporting a wastewater spill of 20,000 gallons in Sanibel Island. Caller stated that the spill came from a privately owned lift station (Coquina Beach Condos). Pumps not operational due to tripped breakers. | 623 Nerita St, Sanibel | none |  |  | 20000 | equipment |  |  | Southern Utilities/Coquina Beach Condos
| 2013-07-10 | 130p | Charlotte | SD | 7/7/2013 - 7/9/2013. | Robert Ruth | City of Punta Gorda | Poor pipe bedding caused split resulting in 2000 gals spilled onto ground. Repaired pipe, vacuumed driveways/swales, limed affected area. | Madrid Blvd & Tamiami Trl, Punta Gorda | vac & lime |  |  | 2000 | break-in-line | 1500 |  | City of Punta Gorda
4594 | 2013-07-11 | 340p | Sarasota | SD | 7/11/2013 15:40 ET | Jim | Novack Environmental Services | Caller reports that 1,500 gallons of raw sewage/rainwater was released from a reclamation facility due to excessive rainfall in the area. The release did enter an unnamed canal. The release did not affect any drinking water. Contractor is liming the area. | 3005 Fair Wind Drive, Nokomis | lime |  |  | 1500 | rain |  | retention pond | Novack Environmental Services
4608 | 2013-07-12 | 801a | Lee | SD | 7/12/2005 12:00 ET | Natasha Alveshire | Call Back Number 1: 239-948-8649 ¦Address: 26511 Snowberry Lane Bonita Springs FL, 34135-6191 | Ongoing wastewater overflow from a manhole in front of the callers home in Bonita Springs. She reported this has been ongoing for the past eight years. The homeowner called the local wastewater utility, They stated the system is privately owned and there is nothing they can do about it. State assistance has been requested. | 26511 Snowberry Lane, Bonita Springs | none |  |  | unknown | unknown |  |  | Unknown
4623 | 2013-07-12 | 425p | Collier | SD | 7/12/2013 16:25 ET | John Short | City of Immokalee | Caller reports that approximately 3,000 gallons of effluent treated water was released as a deep well line was being repaired in Immokalee. The release was contained onsite. | 140 White Way, Immokalee | none |  | treated | 3000 | repair |  |  | City of Immokalee
4624 | 2013-07-12 | 433p | Collier | SD | 7/12/2013 16:33 ET | John Short | City of Immokalee | Caller reports that approximately 500 gallons per minute of wastewater has been released in Immokalee while crews have been trying to install a new pump system since approximately Tuesday July 9th. The release is a raw sewage mix and has not entered any storm drains, surface water, or drinking water. | Lat: 26.4184, Long: -81.43104 | in-progress |  |  | 30000 | repair |  |  | City of Immokalee
4692 | 2013-07-15 | 928a | Lee | SD | 7/14/2013 20:00 ET | Lina Quintero | US Water-Del Prado WWTP | US Water Services reports a treated effluent water spill in North Ft. Myers. Caller stated that a 12 inch line broke causing the spill. | 4100 Del Prado Blvd, North Ft. Myers | none |  | reclaimed | unknown | break-in-line |  |  | US Water Services
| 2013-07-15 | 300p | Collier |  | 7/14/2013 14:00 ET | David Haskins | Collier County Collections | 500 gals spilled from LS due to high flows during heavy rainfall. Mixture of sewage and stormwater vacuumed from on-site containment area. Area limed. | 2732 Francis Ave, Naples | vac & lime |  |  | 500 | rain | 500 |  | Collier County Utilities
4778 | 2013-07-17 | 407p | Sarasota | SD | 7/17/2013 11:00 ET | Steve Bothaft | Sarasota County-Bee Ridge WRF | Caller reported a wastewater release greater than 10,000 gallons in Sarasota. Blockage in line caused manhole to overflow. A Storm water system and surface waters were affected. Clean up actions were taken. | Mauna Loa Blvd & Luzon Way, Sarasota | vac & lime |  |  | >10,000 | blockage | 10000 | retention pond | Sarasota County
4781 | 2013-07-17 | 534p | Desoto | SD | 7/17/2013 17:00 ET | Julie Karleskint | Hazen and Sawyer Engineering | Caller reports a Wastewater Release in Arcadia. Due to heavy rains impacting the area, two manholes are discharging storm water/sewage mix at a rate of 100 gallons per minute. | Parker Ave, Oak Street, Arcadia | planned |  |  | 100/min | rain |  |  | Hazen and Sawyer Engineering
| 2013-07-17 | 902a | Charlotte | SD | 7/16/2013 13:30 ET | Lloyd Eason | East Port WRF | 150 gals spilled due to line break caused by deterioration due to age. Sewage in swale drained back to forcemain. Repaired line. | 2443 Amrose Ln, Port Charlotte | unknown |  |  | 150 | break-in-line | 100 |  | Charlotte County Utilities
| 2013-07-19 | 130p | Monroe | SD | 7/18/2013 19:00 ET | Melisa Rotteveel | US Water-City of Marathon Area 4 | 500 gals overflowed from mudwell of SBR due to heavy rains. All discharge remained on site, affected area cleaned. | 140 Sombrero Beach Rd, Marathon | unknown |  | partially treated | 500 | rain |  |  | City of Marathon
| 2013-07-19 | 215p | Monroe | SD | 7/18/2013 17:50 ET | Melisa Rotteveel | US Water-City of Marathon Area 7 | Less than 50 gals of effluent/suspended solids discharged onto grounds from mudwell due to heavy rains. Contained on-site, area cleaned. | 59275 Overseas Highway, Marathon | unknown |  | partially treated | <50 | rain |  |  | City of Marathon
| 2013-07-23 | 215p | Lee | SD | 7/23/2013 19:00 ET | Rich Sims | Lee County Utilities | 200 gals seepted out around manhole due to blockage. Cleared with vac truck, washed and recovered spill areas. | 20452 Torre Del Lago, Fort Myers | vac |  |  | 200 | blockage | 50 |  | Lee County Utilities
| 2013-07-25 | 430p | Lee | SD | 7/24/2013 16:45 ET | Lina Quintero | US Water-Del Prado WWTP | 400 gals reclaimed spilled when line broke after years of deterioration after it was hit by contractor during pole installation. | 8050 Bayshore Rd, North Fort Myers | none |  | reclaimed | 400 | break-in-line |  |  | US Water
5052 | 2013-07-27 | 534p | Sarasota | SD | 7/27/2013 17:00 ET | Jason Brown | Sarasota County-Bee Ridge WRF | Caller reports that 1,000+ gallons of raw sewage has been released in Sarasota due to a force main break. The release has entered a storm pond but will be able to vacuum the area out. The release has not entered any source of drinking water. The area will be limed once the spill has been cleaned up. All samples below limits as of 8/9/13. | 3456 Founders Club Drive, Sarasota | vac & lime |  |  | >1000 | equipment | 24000 | storm pond | Sarasota County
5080 | 2013-07-29 | 707a | Sarasota | SD | 7/27/2013 17:00 ET | Roger Hostetler | Sarasota County-Siesta Key AWWTP | Caller reports a wastewater release of 2000 gallons in Sarasota due to power surge at LS. A Storm water system and surface waters were affected. Samples pulled and area limed. | 5640 Rand Blvd, Sarasota | vac & lime |  |  | 2000 | power | 1500 | retention pond | Sarasota County
| 2013-07-29 | 911a | Collier | SD | 7/27/2013 11:00 ET | Jim Gammell | Collier County Collections | Gravity line overwhelmed by heavy rain resulting in 100 gallons of stormwater/wastewater being discharged from manhole. Vac truck drained line and removed surrounding water. | 418 Willet Ave, Naples | vac |  |  | 100 | rain | 100 |  | Collier County Utilities
5133 | 2013-07-30 | 324p | Lee | SD | 7/30/2013 14:45 ET | Lina Ntero | US Water Services | Caller is reporting a 2,000 gallon raw sewage spill in LeeHigh Acres. The spill came from a broken 8 inch main line. The spill has been contained and clean up actions are in progress. No waterways or storm water systems have been impacted. | Lee St, Leonard Blvd N, LeeHigh Acres | vac truck |  |  | 2000 | break-in-line |  |  | US Water Services
| 2013-07-30 | 1100a | Highlands | SD | 7/28/2013 17:00 ET | Lisa Holmes | Pugh Utilities-Fairmount | Berm of perc pond was breached due to abnormally heavy rains. Berm was repaired, but unknown how much effluent may have discharged off site. | Fairmount WWTP | none |  | treated | unknown | rain |  |  | Fairmount Utilities
| 2013-07-30 | 455p | Sarasota | SD | 7/30/2013 15:00 ET | Gerald Boyce | City of Sarasota AWWTF | Stoppage on city side of cleanout caused 25 gallons to spill onto ground/into storm gutter area. Vac truck washed down area and removed excess water. Area limed. | 2016 Mabel Long Ct, Sarasota | vac & lime |  |  | 25 | blockage | 25 |  | City of Sarasota
5211 | 2013-08-02 | 307p | Lee | SD | 8/2/2013 10:00 ET | Richard Moulton | City of Fort Myers-Central | Caller reports approximately 1,500 gallons of raw sewage has been released in Fort Myers from manhole due to excessive rainfall. The release is entering the Caloosahatchee River. The release is being treated with bleach. No source of drinking water has been affected. | 1215 Alhambra Dr, Fort Myers | HTH |  |  | 1500 | rain |  | Caloosahatchee River | City of Fort Myers
| 2013-08-02 | 310p | Sarasota | SD | 8/2/2013 11:00 ET | Gerald Boyce | City of Sarasota AWWTF | 5 gals overflowed from manhole due to grease blockage. Vacuumed line, washed down, limed. | 111 North Tamiami Tr, Sarasota | vac & lime |  |  | 5 | FOG | 5 gal |  | City of Sarasota
| 2013-08-02 | 450p | Sarasota | SD | 8/7/2013 00:00 ET | Patricia Nihart | Sarasota County Utilities | 100 gals spilled into containment area during work on north south connection. Affected area limed, work area backfilled, project completed. | Border Rd & Laurel Rd, Sarasota | lime |  |  | 100 | maintenance |  |  | Sarasota County Utilities
5280 | 2013-08-05 | 522p | Sarasota | SD | 8/5/2013 08:00 ET | Steve Bothast | Sarasota County-Bee Ridge WRF | Caller is reporting a raw sewage release of approximately 1,000 gallons in Sarasota. The release came from a small crack in the force main. No surface waters or storm water systems have been impacted. Clean up actions have been completed. | Bee Ridge Rd & Honore Ave, Sarasota | vac & lime |  |  | 1000 | break-in-line | 1000 |  | Sarasota County
| 2013-08-05 | 920a | Sarasota | SD | 8/6/2013 14:00 ET | Patricia Nihart | Sarasota County Utilities | 200 gals spilled into containment area while tieing in new forcemain at Bent Tree LS. Area pumped down and limed. | 7650 Bee Ridge Rd, Sarasota | vac & lime |  |  | 200 | maintenance | 200 |  | Sarasota County
5292 | 2013-08-06 | 157p | Sarasota | SD | 8/5/2013 15:15 ET | Gerald Boyce | City of Sarasota AWWTF | Caller is reporting a 7,500 gallon treated effluent spill in Sarasota. Contractor hit reuse irrigation line. Valve closed, contractor to make repairs. Caller stated that the spill entered Sarasota Bay. | Main St & Mira Mar Ct, Sarasota | none |  | reclaimed | 7500 | contractor |  | Sarasota Bay | City of Sarasota
| 2013-08-07 | 900a | Sarasota | SD | 8/6/2013 09:15 ET | Gerald Boyce | City of Sarasota AWWTF | 400 gals of raw spilled due to grease blockage in main line. Vac truck cleared line and washed down area. Lime applied. Affected storm drains flow to Hog Creek. Samples pulled. | North Tamiami Tr & 11th St, Sarasota | vac & lime |  |  | 400 | FOG | 200 | Hog Creek | City of Sarasota
| 2013-08-08 | 148p | Collier | SD | 8/7/2013 11:30 ET | Danette Kinasczuk | Collier County-North | 500 gals reclaimed released due to break in private Collier Co Transportation 3" irrigation line. Water absorbed into grassy area and stormwater system. | 6784 Goodlette Frank Rd, Naples | none |  | reclaimed | 500 | break-in-line |  |  | Collier County Utilities
5368 | 2013-08-09 | 107p | Charlotte | SD | 8/9/2013 10:15 ET | Ed McCampbell | City of Punta Gorda WWTP | Caller reports that 200,000 gallons of raw sewage was released in Punta Gorda due to a contractor collapsing a 30 inch main line. The release was contained on site but did enter a storm drain that was sand bagged preventing further contamination. No surface or drinking water was affected. | 30999 Bermont Road, Punta Gorda | vac & lime |  | partially treated | 200000 | contractor | 190000 |  | City of Punta Gorda
| 2013-08-09 | 900p | Collier | SD | 8/9/2013 21:00 ET | Kevin Rudy | Collier County Collections | 4 gallons spilled due to blocked gravity line. Vac truck cleared blockage, cleaned and disinfected area with bleach. | 1984 Timberline Dr, Naples | bleach |  |  | 4 | blockage |  |  | Collier County Collections
5391 | 2013-08-10 | 1111a | Lee | SD | 8/10/2013 11:11 ET | Lina Quintero | US Water-Del Prado WWTP | Caller reports a Treated Effluent Release of 875,000 gals in North Fort Myers. Reuse well overflowed due to heavy rains. No waterways impacted. | 4100 Del Prado Blvd, North Fort Myers | none |  | treated | 875000 | rain |  |  | US Water Services
5400 | 2013-08-10 | 513p | Collier | SD | 8/10/2013 17:13 ET | Kevin | Collier County-North | Caller reports that 4,750 gallons of reclaim water was released from a break in a gravity line in Naples. No cleanup actions were necessary for the release. | 8039 Reef Point, Naples | none |  | reclaimed | 4750 | break-in-line |  |  | Collier County Utilities
5412 | 2013-08-11 | 603p | Lee | SD | 8/11/2013 18:03 ET | Pete Frye | Concerned Citizen | Caller is reporting a large amount of raw sewage in the canal behind his house in Ft. Myers. Caller stated that he does not live near a water treatment facility, and does not know where the sewage is coming from. The caller did state that the sewage came in with the high tide. Caller is requesting a call back from DEP. | 260 Flamingo St , Fort Myers Beach | none |  |  | unknown | unknown
5440 | 2013-08-13 | 1106a | Lee | SD | 8/9/2013 18:30 ET | Richard Moulton | City of Fort Myers-Central | Caller is reporting a wastewater spill over 1,000 gallons in Ft. Myers. The spill occurred due to excessive rainfall. The wastewater was a mixture of untreated wastewater and rain water. The mixture entered the Caloosahatchee River. | 1215 Alhambra Dr, Fort Myers | HTH & lime |  |  | >1000 | rain |  | Caloosahatchee River | City of Fort Myers
| 2013-08-14 | 338p | Collier | SD | 8/14/2013 14:15 ET | Danette Kinasczuk | Collier County-South | 800 gals reclaimed water released from gasket on 16" IQ water line. Absorbed into surrounding grassy area. | 111 Palm Dr, Naples | none |  | reclaimed | 800 | break-in-line |  |  | Collier County Utilities
| 2013-08-15 | 445p | Sarasota | SD | 8/14/2013. | Patricia Nihart | Sarasota County Utilities | 14,000 gallons spilled into excavated containment area while contractor was cutting and capping line. Sewage contained, removed by vac truck, area limed. | Iona Rd, Sarasota | vac & lime |  |  | 14000 | contractor | 14000 |  | General Contracting Services
5527 | 2013-08-16 | 137p | Lee | SD | 8/16/2013 09:30 ET | Melisa Rotteveel | US Water-South Seas WWTF | Caller reports 1,500 gallons of raw sewage was released in Captiva Island due to pump failure at a lift station. The release was contained on-site. No surface water, drinking water, or storm water systems were affected. The affected area was limed. | 5400 Plantation Road, Captiva | limed |  |  | 1500 | equipment |  |  | FGUA
| 2013-08-17 | 1045a | Sarasota | SD | 8/16/2013 18:20 ET | Robert Seibel | Sarasota County-CCU WRF | Digester transfer pumps inadvertently left on and digester overflowed onto ground and into onsite stormwater pond. Sludge vacuumed and limed. Samples pulled. All samples below limits by 8/26/13. | 7905 South McIntosh, Sarasota | vac & lime |  | sludge | 500 | negligence |  |  | US Water-South Seas WWTF
| 2013-08-17 | 608p | Lee | SD | 8/17/2013. | Melisa Rotteveel | US Water-South Seas WWTF | Both LS pumps down/blocked, causing 150 gals to discharge onto adjacent ground. Pumps pulled, cleaned, reinstalled. Area cleaned. | South Seas WWTP | unknown |  |  | 150 | equipment |  |  | FGUA
5653 | 2013-08-21 | 839a | Sarasota | SD | 8/20/2013 20:00 ET | David Abene | City of Venice-Eastside WRF | Caller is reporting a treated effluent spill of 3,000 gallons in Venice. The spill entered a nearby storm drain. | 451 Zacapa Ave, Venice | none |  | reclaimed | 3000 | break-in-line |  |  | City of Venice
| 2013-08-21 | 745a | Lee | SD | 8/21/2013 08:20 ET | Jerry May | Bonita Springs-West WRF | Lift station backed up due to transfer switch failure causing 300 gals to overflow from manhole. Area hosed down, ditched vacuumed and limed. | 9855 Treasure Cay, Bonita Springs | vac & lime |  |  | 300 | equipment | 250 |  | Bonita Springs Utilities
5712 | 2013-08-22 | 208p | Collier | SD | 8/21/2013 14:08 ET | Steve | Collier County Collections | Collier County Utilities reports a Wastewater Release in Naples. 18,000 gallons of sewage/stormwater mix released from a Force Main due to possible issue with isolation valve. Clean-up actions completed. | Immokalee Rd & 39th Ave, Naples | vac & lime |  |  | 18000 | equipment | 40,000 (sw+ww) |  | Collier County Utilities
5713 | 2013-08-22 | 212p | Collier | SD | 8/21/2013 22:00 ET | Danette Kinaszczuk | Collier County-North | Caller reports a treated effluent release of approximately 250,000 gallons in Naples. No clean up actions are needed. | 615 Venezia Grande Drive, Naples | none |  | reclaimed | 250000 | break-in-line |  |  | Collier County Utilities
5703 | 2013-08-22 | 1234p | Desoto | SD | 8/22/2013 09:00 ET | Melisa Rotteveel | US Water-Spring Lake Youth Academy | Caller reports that 1,000 gallons of raw sewage was released in Arcadia due to pump failure at a lift station. The release did enter into a ditch that flows into the Peace River. No drinking water was affected. Vacuum trucks were called into clean up any remaining waste. All samples below limits. | 8806 Southwest Start Center Street, Arcadia | vac |  |  | 1000 | equipment |  |  | US Water Services
| 2013-08-24 | 700a | Collier | SD | 8/24/2013. | Howard Brogdon | Collier County-North | WWTP experienced brief power outwage resulting in loss of SCADA controls. Lift station containing blend of WTP process water and sanitary sewer overflowed. Area disinfected with chlorine solution. | 8005 Vanderbuilt Beach Rd Ext, Naples | bleach |  |  | 660 | power |  |  | Collier County Utilities
5785 | 2013-08-26 | 947a | Desoto | SD | 8/24/2013 20:05 ET | Fred Louis | City of Arcadia | Caller reports a release of approximately 20,000 gallons of wastewater in the City of Arcadia. Manholes surcharged due to I&I from heavy rains. A Storm water system and the Peace River have been affected. Clean up actions are unknown. | Parker Ave & Magnolia St, Arcadia | HTH |  |  | 20000 | rain |  | stormwater/Peace River | City of Arcadia
5820 | 2013-08-27 | 236p | Sarasota | SD | 8/27/2013 07:30 ET | Gerald Boyce | City of Sarasota AWWTF | Caller is reporting a wastewater spill of 3,000 gallons in Sarasota. Gravity line clogged with sand. Caller states that the spill entered a storm water system that flows to a ravine. Caller states that clean up and testing are underway. Vac truck washed down and vacuumed up area, limed applied, samples pulled. | Loma Linda St & Shade Ave, Sarasota | vac & lime |  |  | 3000 | blockage | 1000 | storm drain/ditch | City of Sarasota
| 2013-08-27 | 907a | Lee | SD | 8/26/2013 08:30 ET | David Vallandingham | City of Cape Coral | 8" force main cracked resulting in 100 gals spilled. Spill contained and removed with vac truck. Line repaired, area limed. | 5100 Pelican Blvd, Cape Coral | vac & lime |  |  | 100 | break-in-line |  |  | City of Cape Coral
5839 | 2013-08-28 | 1152a | Lee | SD | 8/28/2013 11:52 ET | Andy Koebold | Bonita Springs Utilities | Caller reports a Wastewater Release in Bonita Springs. 2,500 gallons of raw sewage released from a Lift Station due to a Power Failure. Repairs and clean-up actions in progress. | 10911 Bonita Beach Road, Bonita Springs | in-progress |  |  | 2500 | power |  |  | Bonita Springs Utilities
5851 | 2013-08-29 | 729a | Charlotte | SD | 8/28/2013 15:30 ET | Brian Kovzelove | Charlotte County-West Port | 4,000 gallons of raw sewage released in the Port Charlotte area due to a damaged line at a construction site. A vehicle ran over the line. No waterways affected. Clean-up and repairs have been completed. | 15776 Aldana Cir, Port Charlotte | vac & lime |  |  | 4000 | accident | 3600 |  | Charlotte County Utilities
| 2013-08-29 | 1045a | Highlands | SD | 8/28/2013 21:30 ET | Dan Stroup | City of Sebring | Force main exiting check valve on pump discharge seperated causing less than 1000 gals to spill on ground. Lift station isolate, repairs made, site raked and limed. | 2101 Timber Ln, Sebring | lime |  |  | <1,000 | break-in-line |  |  | City of Sebring
| 2013-08-29 | 954a | Lee | SD | 8/29/2013 09:54 ET | Jerry May | Bonita Springs-West WRF | 200 gals spilled from manhole into parking lot. Affected area limed. | 28388 Beaumont, Bonita Springs | lime |  |  | 200 | equipment |  |  | Bonita Springs Utilities
5872 | 2013-08-30 | 1026a | Collier | SD | 8/29/2013 16:15 ET | Martin McAndrew | Collier County-South | Caller reports treated effluent release in Naples. A 4" irrigation line burst releasing 2000 gallons of treated effluent into a grassy area. No clean-up actions required and repairs have been completed. | 8846 Maripos Ct, Naples | none |  | reclaimed | 2000 | break-in-line |  |  | Collier County Utilities
5880 | 2013-08-30 | 230p | Charlotte | SD | 8/30/2013 10:00 ET | Mike Catalano | Charlotte County-East Port | Charlotte County Utilities reports a Wastewater Release in Punta Gorda. 14,400 gallons of raw sewage released from a gravity line due to a power failure at a Lift Station. All repairs and clean-up actions have been completed. The release impacted a storm drain that discharges into Lake Zappa. | 25147 Nocturne Lane, Punta Gorda | vac & lime |  |  | 14400 | power | 6000 | Lake Zappa | Charlotte County Utilities
| 2013-09-01 | 900a | Sarasota | SD | 8/31/2013 18:30 ET | David Guilmette | City of Venice-Eastside WRF | 50 gals overflowed from cleanout when plumber removed it while attempting to unblock discharge line. Flowed into stormdrain. Area disinfected with lime. | 1330 Tarpon Center Dr, Venice | lime |  |  | 50 | contractor |  | storm water | City of Venice
| 2013-09-03 | 739a | Collier | SD | 9/2/2013 21:15 ET | Danette Kinaszczuk | Collier County-North | 900 gals of reclaimed water released on private side. Absorbed into surrounding grassy area and stormwater system. | 8855 Ventura Dr, Naples | none |  | reclaimed | 900 | break-in-line |  |  | Collier County Utilities
| 2013-09-03 | 647p | Lee | SD | 8/30/2013. | Karen Doiron | Island Vista MHP | 700 gals spilled from manhole due to LS pump failure, heavy rains and I&I issues. Pump replaced, vac trucks called in. | Island Vista MHP | vac |  |  | 700 | equipment |  |  | Equity Lifestyle Properties
6005 | 2013-09-04 | 829a | Charlotte | SD | 9/4/2013 14:20 ET | John McGinnis | Charlotte County-Rotunda | Charlotte County Utilities reports a Treated Effluent Release in Placida. 76,000 gallons of treated effluent released due to a line break. Repairs have been completed. No clean-up actions required. | 10045 Links Lane, Placida | none |  | reclaimed | 76000 | break-in-line |  |  | Charlotte County Utilities
| 2013-09-05 | 430p | Sarasota | SD | 9/5/2013 12:00 ET | Steve Bothast | Venice East WRF | 800 gals spilled due to crack in PVC forcemain. Line repaired, spill vacuumed and limed. | 101 Venice Palms Blvd, Venice | vac & lime |  |  | 800 | break-in-line | 800 |  | Sarasota County
6068 | 2013-09-06 | 1106p | Lee | SD | 9/6/2013 22:30 ET | Andy Koebel | Bonita Springs Utilities | An estimated 8,000 gallons of untreated domestic wastewater overflowed from a lift station in the Bonita Springs area due to hydraulic overload from heavy rains. The release has stopped. Some of the release drained into Oak Creek. Clean-up actions will be conducted by the responsible party. | Front St & Pennsylvania Ave, Bonita Springs | lime |  |  | 8000 | rain |  | Oak Creek | Bonita Springs Utilities
| 2013-09-06 | 1210p | Lee | SD | 9/5/2013 15:00 ET | David Vallandingham | City of Cape Coral | Manhole became surcharged resulting in 50 gals discharged onto ground. Spill contained and removed with vac truck. Disinfected with lime. | 4959 Viceroy St, Cape Coral | vac & lime |  |  | 50 | FOG |  |  | City of Cape Coral
6077 | 2013-09-07 | 1154a | Collier | SD | 9/7/2013 02:00 ET | Millie Kelley | Collier County Collections | Caller reports that 42,800 gallons of raw sewage has be released in Naples due to heavy rain and lightning striking a lift station. The release entered a containment retention pond around the lift station. No surface waters or drinking water was affected. Vacuum trucks were brought in to clean up the release. | Heather Lane & Valewood Dr, Naples | vac & lime |  |  | 42800 | power | 42,100 gals |  | Collier County Utilities
| 2013-09-10 | 520p | Lee | SD | 9/10/2013 12:00 ET | Lina Quintero | US Water-Del Prado WWTP | 4" forcemain hit by landscaping contractor causing 200 gals to spill onto ground. Repairs complete, area cleaned. | 2021 N Tamiami Tr, North Fort Myers | vac |  |  | 200 | contractor | 200 |  | US Water
6135 | 2013-09-11 | 729a | Sarasota | SD | 9/11/2013 01:20 ET | Jim Petrusky | City of Venice-Eastside WRF | 36,000 gallons of treated wastewater spilled on-site in the Venice area due to a ruptured 2-inch line (reclaim feed line to grit system). No waterways affected. No clean-up actions required. Repairs have been completed. | 3510 Laurel Road, Venice | none |  | reclaimed | 36000 | break-in-line |  |  | City of Venice
| 2013-09-12 | 300p | Highlands | SD | 9/12/2013 12:00 ET | Dan Stroup | Francis I MHP | Contractor broke forcemain during directional boring causing unknown amount of raw sewage to spill. City removed 650 gals by vac truck, then contacted responsible party. Responsible party (Francis I) made repairs to damaged line. | 3115 US 27 S, Sebring | vac |  |  | unknown | contractor | 650 gals |  | Francis I MHP
| 2013-09-16 | 755a | Collier | SD | 9/16/2013. | Howard Brogdon | Collier County-North | Approx 660 gals spilled due to loss of SCADA communications following brief power outage. Lift station overflowed as a result. Adjustments made to power system and alarm routing to prevent reoccurance. Affected area disinfected with Cl2 solution. | 8005 Vanderbuilt Beach Rd Ext, Naples | disinfected |  |  | 660 | power |  |  | Collier County Utilities
6252 | 2013-09-16 | 157p | Sarasota | SD | 9/16/2013 13:57 ET | Richard Retz | Aqua Utilities-Fruitville | Caller is reporting an on-going reclaimed water release in Sarasota. The release is on going, releasing about 300 gallons a minute. At this time they have not contained the release. The caller stated that no clean up actions are required, the water has been treated. Ceased discharging on Friday 10/18/2013 at approximately 9:00 am | Lorainre Rd, Sarasota | none |  | reclaimed | 18000 | rain |  | Longbranch Tributary to Cooper Creek | Aqua Utilities
6278 | 2013-09-17 | 158p | Lee | SD | 9/16/2013 16:00 ET | Terry Handlin | Gateway Services | Caller reports a treated effluent spill of approximately 100,000 gallons in Ft. Myers. No storm drains or waterways were affected. Gateway Service conducted the cleanup. | Lat: 26.55651, Long: -81.7504 | pumped up release |  | treated | 100000 | break-in-line |  |  | Gateway Services
6290 | 2013-09-17 | 825a | Collier | SD | 9/17/2013 15:00 ET | Jim Gammell | Collier County Collections | Caller is reporting a wastewater release of approximately 2450 gallons total from multiple lift stations in Naples. The caller stated that the release may have entered a storm drain, but the county is doing further testing to confirm. No other water systems have been impacted. Clean up actions have been taken. All samples below limits as of 9/23/13. | 2732 Francis Ave, Naples | vac & lime |  |  | 2450 | rain | 200 gals | storm water | Collier County Utilities
| 2013-09-17 | 209p | Lee | SD | 9/17/2013 08:00 ET | Dennis Morgan | City of Cape Coral | Check valve failed causing overwhelming backflow resulting in 50 gals spilled on ground. Check valve replaced, spill was vacuumed and limed. | 1029 Diplomat Pkwy, Cape Coral | vac & lime |  |  | 50 | equipment |  |  | City of Cape Coral
| 2013-09-18 | 825a | Collier | SD | 9/17/2013 12:30 ET | Jim Gammell | Collier County Collections | ARV malfunctioned causing 100 gallons to spill onto ground and into storm drain. ARV replaced, spill disinfected with lime, canal that storm drain flows into was sampled and all samples were below 800 cfu. | NE corner of Santa Barbara & Davis Blvd, Naples | lime |  |  | 100 | equipment |  |  | Collier County Utilities
6310 | 2013-09-19 | 834a | Lee | SD | 9/18/2013 18:00 ET | Andy Koebel | Bonita Springs West WRF | Caller is reporting a release of 5,000 gallons in Bonita Springs. The release occurred at a force main, and was caused by heavy rains. The release was secured and clean up actions have been taken. Only a nearby ditch was impacted by the release, no other surface waters or storm waters were impacted. | 27046 El Rio Dr, Bonita Springs | vac/lime |  |  | 5000 | rain | 1000 |  | Bonita Springs Utilities
6315 | 2013-09-19 | 1139a | Lee | SD | 9/18/2013 11:00 ET | Andy Koebel | Bonita Springs Utilities | Caller reports that 750,000 gallons of treated effluent water was released due to an electrical malfunction of level indicator in Bonita Springs. No cleanup actions were necessary. | Elementary Way, Bonita Springs | none |  | treated | 750000 | equipment |  |  | Bonita Springs Utilities
| 2013-09-19 | 411p | Collier | SD | 9/17/2013 11:00 ET | Danette Kinaszczuk | Collier County-North | Approx 200 gals reclaimed water released from private line. Water absorbed into surrounding grassy area. | 9246 Troon Lakes Dr, Naples | none |  | reclaimed | 200 | break-in-line |  |  | Collier County Utilities
| 2013-09-19 | 900a | Lee | SD | 9/18/2013 20:00 ET | Jerry May | Bonita Springs West WRF | Master lift station #360 was unable to keep up with high flows during heavy rainfall resulting in 600 gallons spilled on the ground. Spill area was vacuumed and limed. | Bonita Beach Rd, Bonita Springs | vac & lime |  |  | 600 | rain |  |  | Bonita Springs Utilities
| 2013-09-19 | 1100a | Lee | SD | 9/18/2013 17:00 ET | Richard Sims | Fort Myers Central WWTP | Approx 750 gallons spilled during heavy rains from disloged manhole and several cleanouts (w/out caps). Smoke testing to identify I&I sources. Spill disinfected with lime. | 5441 Palm Beach Blvd, Fort Myers | lime |  |  | 750 | rain | 500 gals |  | Lee County Utilities
| 2013-09-19 | 1210p | Sarasota | SD | 9/19/2013 07:00 ET | Bob Hogan | Sarasota County Utilities | Approx 500-800 gals spilled from manhole at hillview lift station due to heavy rains. Storm water system affected. Samples pulled. | Shamrock Blvd & Willow Cir, Venice | unknown |  |  | 800 | rain |  |  | Sarasota County Utilities
| 2013-09-19 | 1100a | Lee | SD | 9/18/2013 17:00 ET | Rich Sims | City of Fort Myers-Central | 750 gals spilled from disloged manhole and several clean outs due to heavy rains/infiltration. Area limed. | 5441 Palm Beach Blvd, Fort Myers | vac & lime |  |  | 750 | rain | 500 |  | City of Fort Myers
6343 | 2013-09-20 | 344p | Lee | SD | 9/20/2013 12:45 ET | Andy Koebel | Bonita Springs Utilities | Caller reports that 6,000 gallons of raw sewage has been released in Bonita Springs due to a force main break. The release did enter into a storm drain that leads to an unknown location. No surface or drinking water was affected. The release is being vacuumed and the area is being limed. | 24940 South Tamiami Trail, Bonita Springs | vac & lime |  |  | 6000 | break-in-line | 2000 gals |  | Bonita Springs Utilities
| 2013-09-20 | 1015a | Sarasota | SD | 9/19/13 13:30 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 150 gals spilled when contractor's excavation equipment struck/damaged LS temporary bypass main. Washed down, vacuumed, limed. Approx 100 gals of spill entered storm water inlet to Sarasota Bay. Samples pulled. | 34 South Gulfstream, Sarasota | vac & lime |  |  | 150 | contractor | 50 | Sarasota Bay | Spectrum
| 2013-09-23 | 900p | Sarasota | SD | 9/23/2013. | Victor Carlano | Venice Gardens WRF | 800 gallons overflowed from LS due to heavy rains. Pumps could not keep up with I&I. Vacuumed, limed. All samples below limits as of 9/30/13. | 326 Hillview Dr, Venice | vac & lime |  |  | 800 | rain |  |  | Sarasota County Utilities
| 2013-09-23 | 1100a | Sarasota | SD | 9/19/2013. | Bill McKee | Aqua Utilities-Fruitville WWTF | 500 gals spilled due to manhole failure caused by heavy rainfall. Stormwater system affected. Area limed, samples collected. | 1518 Grantham Dr, Sarasota | lime |  |  | 500 | rain |  |  | FGUA
6425 | 2013-09-24 | 1016a | Lee | SD | 9/24/2013 10:16 ET | Lina Quintero | US Water-Del Prado WWTP | US Water is reporting a treated effluent spill of 751,000 in North Ft. Myers. The spill was caused by excessive rainfall and was contained to the North Ft. Myers Wastewater Treatment Facility. Caller stated that no clean up is necessary. UPDATE 9/27/13: 4,576,000 total overflowed from reuse well over course of 3 days. | Lat: 26.72848, Long: -81.88111 | none |  | treated | 4576000 | on-site |  |  | US Water
6433 | 2013-09-24 | 1232p | Sarasota | SD | 9/24/2013 06:30 ET | Jim Petrosky | City of Venice-Eastside WRF | Caller reports a raw sewage release of 27,000 gallons from a reclamation facility in Venice at pre-treatment structure. No storm drains or surface waters were affected. The City of Venice Utilities is conducting the clean up by applying HTH. | 3510 Laurel Road E, Venice | HTH |  |  | 27000 | rain |  |  | City of Venice
6444 | 2013-09-24 | 307p | Lee | SD | 9/23/2013 22:00 ET | Richard Molten | City of Ft. Myers | The City of Ft. Myers is reporting a wastewater spill in Ft. Myers over 1,000 gallons. The spill is entering the Caloosahatchee River. Caller stated that clean up actions are being taken. | Lat: 26.62222, Long: -81.8877 | planned |  |  | > 1000 | rain |  |  | City of Ft. Myers
| 2013-09-24 | 245p | Sarasota | SD | 9/24/2013 14:45 ET | Robert Seibel | Sarasota County-Siesta Key AWWTP | Due to heavy rains, operator opened bypass valve from clarifier to outlet to Grand Canal. Approx 200,000 gallons bypassed. Sampling ongoing. Samples under limits as of 9/27/13. | 5200 Oakmont Place, Siesta Key | unknown |  | partially treated | 200000 | rain |  | Grand Canal | Sarasota County Utilities
6475 | 2013-09-25 | 818a | Lee | SD | 9/24/2013 00:00 ET | John Bolder | City of Fort Myers-Central | City of Ft. Myers is reporting a 3 million gallon release of treated effluent water into Billy's Creek in Ft. Myers. CCC overflowed. Caller states that the excessive rainfall caused the release. | 1501 Raleigh St, Fort Myers | HTH |  | treated | 3000000 | rain |  |  | City of Fort Myers
6477 | 2013-09-25 | 844a | Collier | SD | 9/24/2013 13:30 ET | Frank Clark | Marco Island Utilities | City of Marco Island reports a Wastewater Release due to a broken Force Main. No storm drains or surface waters impacted. Amount of release is unknown at this time. Repairs and clean-up have been completed. | Royal Marco Way & Hideaway Circle, Marco Island | vac & lime |  |  | unknown | break-in-line | 3000 |  | Marco Island Utilities
6478 | 2013-09-25 | 915a | Sarasota | SD | 9/25/2013 09:15 ET | Rick Retz | Aqua Utilities-Fruitville WWTP | Aqua Utilities reports a Wastewater Release in Sarasota. Due to heavy rains impacting the area, multiple manholes are discharging sewage and storm water along Monica Parkway. Clean-up will begin when flood waters recede. | Prudence, 27th St & Randa, Sarasota | planned |  |  | unknown | rain |  | Phillipe Creek | Aqua Utilities
6486 | 2013-09-25 | 1109a | Sarasota | SD | 9/25/2013 13:41 ET | Phil Wagner | Englewood Water District | Englewood Water District is reporting a wastewater spill of 17,000 gallons in Englewood. The wastewater entered a nearby storm retention pond. The area was limed. | 521 River Rd, Englewood | lime |  |  | 17000 | rain |  | retention pond | Englewood Water District
| 2013-09-25 | 1045a | Charlotte | SD | 9/24/2013 21:45 ET | Tom Jackson | City of Punta Gorda WWTP | Sewage holding tank at booster pumping facility (BPF) overflowed through small vent on top of tank due to heavy rains. Less than 100 gals spilled. Contained to site and absorbed into ground. | City of Punta Gorda BPF | none |  |  | 100 | rain |  |  | City of Punta Gorda
6514 | 2013-09-26 | 840a | Sarasota | SD | 9/26/2013 08:40 ET | Mickey Healy | City of Venice-Eastside WRF | A representative with City of Venice Utilities reported that 2500 gallon of wastewater was spilled from 9/24 - 9/25 from a manhole due to heavy rains. Caller advised that some of the spill went into a storm drain. Caller advised that the affected area was vacuumed and covered with lime. | 1100 Laurel Ave, 700 Villas, 400 E Venice Ave, Venice | vac & lime |  |  | 2500 | rain | 600 | Hatchett Creek | City of Venice-Eastside WRF
6516 | 2013-09-26 | 914a | Sarasota | SD | 9/26/2013 09:14 ET | David Hawkins | Sarasota County-Bee Ridge WRF | Sarasota County Utilities reports a Treated Reclaim Release at the Bee Ridge Treatment Plant. So far, 5 million gallons of treated reclaim water have been released from reuse storage pond, and the release is ongoing. This is caused by heavy rains impacting the area. Discharge stopped 10/8/13. All samples below limits by 10/9/13. | 4001 Iona Road, Sarasota | none |  | reclaimed | 56210000 | rain |  | storm water | Sarasota County Utilities
6532 | 2013-09-26 | 230p | Charlotte | SD | 9/24/2013 13:00 ET | Charlie Rine | Charlotte County-East Port | Caller reports that 5,000 gallons of raw sewage has been released in Port Charlotte due to excessive rainfall. No storm systems, surface water, or drinking water was affected by the release. The area was vacuumed and limed. | 22460 Olean Blvd, Port Charlotte | vac & lime |  |  | 5000 | rain | 2000 |  | Charlotte County-East Port
6533 | 2013-09-26 | 234p | Charlotte | SD | 9/24/2013 13:00 ET | Charlie | Charlotte County Utilities | Caller reports that 1,000 gallons of raw sewage has been released in Port Charlotte due to control panel failure at a lift station. No storm systems, surface water, or drinking water was affected by the release. The area was limed. | Hope Well Ave, Neville Terrace, Port Charlotte | lime |  |  | 1000 | equipment |  |  | Charlotte County Utilities
6534 | 2013-09-26 | 247p | Charlotte | SD | 9/24/2013 13:00 ET | Charlie | Charlotte County Utilities | Caller reports that 1,000 gallons of raw sewage has been released in Port Charlotte due to control panel failure at a lift station. No storm systems, surface water, or drinking water was affected by the release. The area was limed. | Lake Worth Blvd, Joseph Street,Port Charlotte | lime |  |  | 1000 | equipment |  |  | Charlotte County Utilities
6535 | 2013-09-26 | 239p | Charlotte | SD | 9/24/2013 13:00 ET | Charlie | Charlotte County Utilities | Caller reports that 1,000 gallons of raw sewage has been released in Port Charlotte due to control panel failure at a lift station. No storm systems, surface water, or drinking water was affected by the release. The area was limed. | 39 Pine Hearst Court, Port Charlotte | lime |  |  | 1000 | equipment |  |  | Charlotte County Utilities
| 2013-09-27 | 1030a | Lee | SD | 9/27/2013. | Melisa Rotteveel | US Water-Lee Mental Health LS | Pump in LS not operational due to root ball in wetwell interfering with floats. 500 gals spilled onto ground. Root ball removed, station pumped down, area vacuumed and limed. | 2789 Ortiz Ave, Fort Myers | vac & lime |  |  | 500 | blockage |  |  | SalusCare, Inc.
| 2013-09-27 | 450p | Lee | SD | 9/27/2013 10:00 ET | Richard Moulton | City of Fort Myers-Central | 500 gals overflowed from manhole due to blockage downstream. Blockage cleared, HTH and lime applied. | Cortez Blvd & Sunset Rd, Fort Myers | HTH & lime |  |  | 500 | blockage |  |  | City of Fort Myers
6578 | 2013-09-28 | 428p | Sarasota | SD | 9/28/2013 15:00 ET | Nicole West | Call Back Number 1: 941-492-2244 | NRC # 1061541 "VERBATIM" CALLER STATED THAT THEIR NEIGHBOR HAS SEWAGE DRAINING INTO THE STORM DRAIN AND INTO THEIR FRONT YARD. | 3147 Galiot Rdoad, Venice | none |  |  | unknown | negligence
6582 | 2013-09-29 | 609a | Collier | SD | 9/28/2013 16:00 ET | Rob Caine | Collier Co. Public Utility | A representative with Collier Co. Public Utility advised over 1,000 gallons of a treated reclaim water released in Naples due to break in 18 inch force main. No waterways were affected, contained to grass area. No clean up actions reported. | Lat: 26.2671, Long: -81.78919 | none |  | treated | 1000 | break-in-line |  |  | Collier Co. Public Utility
6602 | 2013-09-30 | 1120a | Charlotte | SD | 9/28/2013 16:00 ET | Charlie Rine | Charlotte County-East Port | Caller reports a wastewater release of 800-1000 gallons in Port Charlotte. No storm water systems and no surface waters were affected. Clean up actions were taken. | 2425 Picnic St, Port Charlotte | lime |  |  | 1000 | break-in-line | 700-900 |  | Charlotte County Utilities
6618 | 2013-10-01 | 1152a | Charlotte | SD | 10/1/2013 11:53 ET | Stephen Bozman | Charlotte County-East Port | Caller is reporting a line that is starting to seep causing raw sewage to spill out. Approximately 100 gallons has been released. There were no surface waters and no storm water systems were effected. | 3100 Loveland, Port Charlotte | planned |  |  | 100 | break-in-line |  |  | Charlotte County Utilities
6668 | 2013-10-04 | 910a | Lee | SD | 10/3/2013 12:00 ET | Rich Sims | Lee County-Fiesta Village | Lee County Utilities reports a Wastewater Release in Fort Myers. 40,000 gallons of raw sewage released from a broken Force Main (damaged by bore machine reamer). Repairs and Clean-up actions have been completed. No surface waters were impacted. | 7010 Cypress Terrace, Fort Myers | vac & lime |  |  | 40000 | break-in-line | 35000 |  | Lee County Utilities
| 2013-10-08 | 450p | Lee | SD | 9/27/2013 10:00 ET | Richard Moulton | City of Fort Myers-Central | 500 gals overflowed from manhole due to heavy rains. Sewer system was surcharged. HTH and lime applied. | Riverview Trace Ct, Fort Myers | HTH & lime |  |  | 500 | rain |  |  | City of Fort Myers
6766 | 2013-10-09 | 840a | Collier | SD | 10/8/2013 07:00 ET | Melisa Rottezeel | US Water-Hunnington Lake LS | Caller reports a release of approximately 5,000 gallons of wastewater from LS in Naples due to pump failure. A Storm water system has been affected. Clean up actions were taken. | 6398 Hunnington Lake Cir, Naples | vac & lime |  |  | 5000 | equipment |  |  | Hunnington Lakes
6775 | 2013-10-09 | 325p | Sarasota | SD | 9/24/2013 09:00 ET | Gerald Boyce | City of Sarasota AWWTF | Caller is reporting a wastewater spill of an unknown amount in Sarasota. Caller stated that rainfall overloaded the wastewater system in Sarasota causing manholes throughout the City of Sarasota to overflow and enter storm water systems which flow to Sarasota Bay. | Mound St & Osprey St, Sarasota | vac & lime |  |  | > 1000 | rain |  | Stormwater/Sarasota Bay | City of Sarasota
| 2013-10-09 | 1245p | Sarasota | SD | 10/8/2013 17:25 ET | Mickey Healy | City of Venice-Eastside WRF | 200 gals spilled during replacement of degraded sanitary sewer main. Discharge contained in excavation and pumped back into adjacent lift station. | US Business 41 @ City LS #25 | vac |  |  | 200 | repair | 200 |  | City of Venice
6786 | 2013-10-10 | 1027a | Collier | SD | 10/10/2013 09:00 ET | Danette Kinaszezuk | Collier County-South | Caller reporting a Treated Effluent water spill in the city of Naples. There was around 150,000 gallons spilled due do a break in a private line. No clean up actions were needed. | 4030 Lakewood Blvd, Naples | none |  | reclaimed | 150000 | break-in-line |  |  | Collier County Utilities
6797 | 2013-10-10 | 245p | Charlotte | SD | 10/10/2013 13:00 ET | Charlie Rine | Charlotte County-East Port | Caller reports a raw sewage release of approximately 2,000 gallons from a force main in Port Charlotte. The release did not enter any storm drains or surface waters. Charlotte County Utilities has conducted the clean up. | 2483 Ambrose Ln, Port Charlotte | vac & lime |  |  | 2000 | break-in-line | 1500 |  | Charlotte County Utilities
| 2013-10-10 | 1153a | Lee | SD | 10/10/2013 08:00 ET | David Vallandingham | City of Cape Coral | 10 gals spilled due to leaky ARV. Spillage contained in vault, removed with vac truck, and limed. ARV replaced. | 4100 Aqualinda Blvd, Cape Coral | vac & lime |  |  | 10 | equipment |  |  | City of Cape Coral
6808 | 2013-10-11 | 832a | Sarasota | SD | 10/10/2013 11:00 ET | Gerald Boyce | City of Sarasota AWWTF | City of Sarasota reports a Treated Effluent Release of 3,000 gallons due to a Service Line break. No clean-up actions required. | 1038 South Osprey Ave, Sarasota | none |  | reclaimed | 3000 | break-in-line |  | stormwater/Hudson Bayou | City of Sarasota
| 2013-10-13 | 1030a | Sarasota | SD | 10/12/2013 10:39 ET | Gerald Boyce | City of Sarasota AWWTF | Approx 150 gals overflowed from manhole due to partial grease blockage in service line. Vac truck washed down and vacuumed area. Some of spill went into storm inlet. Recovered 3000 gallons from stormwater system. Area disinfected with lime. | 1111 N Tamiami Tr, Sarasota | vac & lime |  |  | 150 | FOG | 150 | stormwater | City of Sarasota
| 2013-10-14 | 1034a | Collier | SD | 10/13/2013 18:00 ET | Danette Kinasczuk | Collier County-North | Approx 500 gals of reclaimed water released. Absorbed into grassy area. | 809 Bentwood Dr, Naples | none |  | reclaimed | 500 | break-in-line |  |  | Collier County Utilities
| 2013-10-14 | 155p | Sarasota | SD | 10/14/2013 10:15 ET | Mickey Healy | City of Venice-Eastside | 500 gals reuse spilled when mowing personnel hit ARV on 2" line. Discharge went to Curry Creek. Line replaced. | 916 Capri Isles Blvd, Venice | none |  | reclaimed | 500 | break-in-line |  | Currey Creek | City of Venice
6864 | 2013-10-15 | 1111a | Lee | SD | 10/15/2013 09:00 ET | Lina Quintero | U.S Water Services Corp | Caller reports a treated effluent release of an unknown amount from a broken pipe line at a wastewater system in Ft. Myers. The release has drained into Powell Creek. U.S Water Services Corp is conducting the clean up. | Ft. Myers | repairs |  | treated | unknown | break-in-line |  | Powell Creek | U.S Water Services Corp
| 2013-10-15 | 905p | Collier | SD | 10/14/2013 17:00 ET | Danette Kinaszczuk | Collier County-North | 200 gals reclaimed water released and absorbed into surrounding grassy area. | 872 Bentwood Dr, Naples | none |  | reclaimed | 200 | break-in-line |  |  | Collier County Utilities
6877 | 2013-10-16 | 1207p | Collier | SD | 10/16/2013 11:30 ET | Rob Cane | Collier County-South | Collier County Utilities reports a Treated Effluent Release in Naples. 100,000 gallons released due to a broken irrigation line. Repairs completed. | Grand Lely Dr, Moore Gate Point Ln, Naples | none |  | reclaimed | 100000 | break-in-line |  |  | Collier County Utilities
6891 | 2013-10-17 | 847a | Sarasota | SD | 10/16/2013 17:00 ET | Trisha Nihart | Sarasota County-Bee Ridge | Sarasota County Utilities reports a Wastewater Release in Sarasota. 7,000 gallons of raw sewage released from a Lift Station due to a clogged pump. The release impacted an unnamed creek adjacent to the Lift Station. Clean-up and repairs have been completed. Sampels below limits as of 10/21/13. | 7650 Bee Ridge Rd, Sarasota | vac & lime |  |  | 7000 | equipment |  | unnamed creek | Sarasota County
| 2013-10-17 | 345p | Desoto | SD | 10/16/2013. | Fred Lewis | William Tyson WWTP | Approx 200 gals overflowed from manhole due to blockage in line. Lined cleared with vac truck, area disinfected with granular chlorine. | unknown | chlorine |  |  | 200 | blockage |  |  | City of Arcadia
6963 | 2013-10-21 | 331p | Desoto | SD | 10/21/2013 12:00 ET | Alex Shannon | DeSoto County Utilities | Caller reports 1,000 gallons of wastewater was released in Arcadia due to leak at FM joint. The release was contained onsite. No surface waters and no storm water systems were affected. | US 17 & Palm Ave, Arcadia | lime |  |  | 1000 | break-in-line |  |  | DeSoto County Utilities
7004 | 2013-10-23 | 352p | Monroe | SD | 10/23/2013 15:52 ET | Lee Carpenter | 305-451-0561 | Caller is reporting a possible wastewater release near Key Largo. The caller stated that the release was between Campers Cove Mobile Home Park and Dolphin Cove. The caller stated that it appeared to be 200 - 300 gallons of raw sewage in the water. No clean up actions have been reported. All information was provided by a third party. | 101640 Overseas Hwy., Key Largo | unknown |  |  | 300 | unknown |  |  | 305-451-0561
| 2013-10-23 | 1130a | Lee | SD | 10/23/2013 09:00 ET | Rich Sims | Lee County-Three Oaks | Less than 200 gals spilled onto ground from cleanouts due to LS pump failure caused by grease buildup interfering with float operation. Station cleaned, spill recovered with vac truck, area limed. | 9425 Scarlett Oak Ave, Estero | vac & lime |  |  | 200 | FOG |  |  | Lee County Utilities
7016 | 2013-10-24 | 100p | Sarasota | SD | 10/24/2013 12:00 ET | Tricia Nihart | Sarasota County-South | Caller reported that there is a waste water spill due to a break in ARV on the force main line at the Sarasota Utility Facility. She reported that the waste water spill has released approx. 1,000 gallons so far and that there is clean up crews on site trying to contain the situation. Spill area was cleaned and limed and 32,000 gals total stormwater and wastewater were recovered. | Knights Tr & Laurel Oak Rd, Sarasota | vac & lime |  |  | > 1,000 | break-in-line | 32000 |  | Sarasota County
7075 | 2013-10-27 | 225p | Monroe | SD | 10/27/2013 14:25 ET | Eddie Moralis | Private Citizen ¦Call Back Number 1: 305-310-8616 | Caller is reporting a possible sewage release behind his residence in Tavernier. The caller stated that he can see and smell sewage in the unnamed canal behind his residence. The caller does not know where the sewage is coming from. No clean up actions have been taken. | 129 Mocking Bird Rd, Tavernier | none |  |  | unknown | unknown |  |  | Private Citizen ¦Call Back Number 1: 305-310-8616
| 2013-10-28 | 424p | Collier | SD | 10/25/2013 15:30 ET | Anthony Milden | Collier County-South | Approx 500 gals of reclaimed water released. Absorbed into grassy area. | 8165 Saratoga Dr, Naples | none |  | reclaimed | 500 | break-in-line |  |  | Collier County Utilities
7088 | 2013-10-28 | 1215p | Sarasota | SD | 10/28/2013 12:15 ET | Mickey Healy | City of Venice-Eastside WRF | Caller is reporting a release of raw sewage in Venice. The caller stated that the release was approximately 5,000 gallons and was being released from a manhole due to blockage in gravity main. The release has been contained and clean up actions have been taken. A near by storm ditch was affected, but no other surface waters were impacted. | US 41 Bypass & Substation Rd, Venice | vac & lime |  |  | 5000 | break-in-line | 4000 | stormwater | City of Venice
| 2013-10-28 | 830a | Sarasota | SD | 10/28/2013 08:30 ET | Rick Newkirk | North Port Utilities | Approx 500-600 gals spilled into containment hole as a result of contractor work. Repaired leak and limed area. | 5355 Pan American Blvd, North Port | lime |  |  | 600 | contractor |  |  | North Port Utilities
| 2013-10-30 | 1015a | Lee | SD | 10/30/2013 09:30 ET | Jerry May | Bonita Springs-West WRF | 500 gals spilled onto ground from LS #189 when both pump overloads tripped. Pumps pulled/checked, overload relays reset/checked. Spill soaked into ground, area limed. | Fountain Lakes Blvd & Caroline Dr, Estero | lime |  |  | 500 | equipment |  |  | Bonita Springs Utilities
| 2013-10-30 | 912a | Desoto | SD | 10/29/2013 19:30 ET | Alex Shannon | DeSoto County Utilities | Mower hit manhole cover damaging inground ARV causing 300 gallons to spill into containment area. ARV replaced, area limed. | US 17, Arcadia | lime |  |  | 300 | break-in-line |  |  | DeSoto County Utilities
| 2013-10-31 | 208p | Collier | SD | 10/30/2013 12:00 ET | Anthony Milden | Collier County-South | 250 gals reclaimed released. Absorbed into grass. | 4333 Beachwood Lake Dr, Naples | none |  | reclaimed | 250 | break-in-line |  |  | Collier County Utilities
7312 | 2013-11-09 | 1015p | Monroe | SD | 11/9/2013 22:15 ET | Dennis | Citizen ¦Call Back Number 1: 780-719-6566 | A concerned citizen reports an unknown amount of sewage was being released in Key Largo. Caller stated that it went into a canal that leads to the Garden Cove which may lead into the Atlantic Ocean. | 30 South Exuma Rd, Key Largo | none |  |  | unknown | unknown |  |  | Citizen ¦Call Back Number 1: 780-719-6566

## Summary-Graphs
Month | # of Spills | Gallons
2013-01-01 | 22 | 0
2013-02-01 | 18 | 0
2013-03-01 | 27 | 0
2013-04-01 | 22 | 0
2013-05-01 | 23 | 0
2013-06-01 | 34 | 0
2013-07-01 | 45 | 0
2013-08-01 | 34 | 0
2013-09-01 | 48 | 0
2013-10-01 | 29 | 0
2013-11-01 | 1 | 0
2013-12-01 | 0 | 0
TOTAL | 303 | 0
Size of Spill | # reported
Unknown | 19 | 6.271%
<1000 | 143 | 47.19%
1000 - 10k | 73 | 24.09%
10,001 - 25k | 14 | 4.62%
25,001 - 100k | 20 | 6.601%
101k - 500k | 8 | 2.64%
> 501k | 5 | 1.65%
282
TOTAL GALS | 0
# of spills | 282
Total | Code | Cause |  | Tot Gallons
8 | Unknown | Unknown /Cause not reported |  | 1400
105 | Break-in-Line | Break in Line |  | 2524430
40 | Equipment | Equipment Malfunction |  | 918900
11 | FOG | Clog or blockage (Fats, Oils, Grease) |  | 1285
17 | Power | Power failure or surge |  | 134015
20 | Contractor | Contractor caused break |  | 242480
3 | Overflow | Overflow |  | 1270
40 | Rain | Heavy Rains / Infiltration of Stormwater |  | 60517250
5 | Negligence | Negligence/Intentional/Error/Vandalism |  | 19000
10 | Accident | Auto accident, 3rd Party action |  | 31820
4 | Repair | Repair work |  | 33700
1 | Hauling | Hauling related |  | 0
0 | Industrial | Industrial Wastewater release |  | 0
0 | Vessel | Vessel or boat release |  | 0
0 | Security | Security issue or breach |  | 0
264 |  |  |  | 64425550
Totals by Utility
|  | Total Spills | Total Gallons | Unknown | Break-in-Line | Equipment | FOG | Power | Contractor | Overflow | Rain | Negligence | Accident | Repair | Hauling
Bonita Springs Utilities |  | 7 | 3100 | 0 | 1 | 4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7
Collier County Utilities |  | 38 | 782590 | 0 | 25 | 2 | 0 | 3 | 2 | 1 | 3 | 0 | 1 | 0 | 0 | 37
Charlotte County Utilities |  | 3 | 77650 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
Lee County Utilities |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Immakolee Water & Sewer |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Marco Island Utilities |  | 4 | 12080 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
North Fort Myers Utilities |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sarasota County Utilities |  | 15 | 56345820 | 0 | 2 | 1 | 0 | 1 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 9
City of Sarasota |  | 8 | 41095 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5

## DOH_Swim_Advisories
District | County | Beach Name | DOH Beach # | Date of Adv. | Date of DOH notification | Summary of Investigation | Date sent to DOH | Cause related to Facility? (Y)