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Department of Environmental Protection - SWD 

Interoffice Memorandum                                                                                                               
TO:
         Steven L. Palmer, P.E., Siting Coordination Office - Tallahassee

THROUGH: Bill Vorstadt, Supervisor, Environmental Resource Permitting, SWD

FROM:        Dennis Pierson, Environmental Resource Permitting, SWD

DATE:         March 2, 2007

SUBJECT:  Supplemental February 23, 2007 Response to my December 29, 2006 RAI

   Drainage Report for Progress Energy Clean Air Project – North Plant (Units 4 and 5)

                     Crystal River, Citrus County


Per your request, the Environmental Resource Permitting, SWD, has reviewed the response dated February 26, 2007, to our request for additional information (RAI) regarding the above-referenced facility and offers the following comments regarding the remaining items to be addressed. The comments are numbered as were our questions in the RAI:

Background: The facility proposes to add new impervious area within Crystal River Units (CR) 4 and 5. The project will include paving existing gravel roads, coal and ash storage areas, new buildings, tanks, temporary laydown areas and parking area. This will create approximately 26 acres of new impervious surface. The facility states that the existing stormwater management system (six drainage basins) was designed for a 25-year 24-hours storm and will provide adequate treatment for the new impervious areas. The addition of 26 acres of impervious surface will require an additional 2.17 ac-ft of treatment volume. Discharge is to the Gulf of Mexico. No floodplain compensation is required.

Comments: 

1., Part II: The applicant will discharge non-contaminated ground water produced by construction activities in accordance with the requirements an IW Generic Permit for this purpose. The permit authorized discharge to surface water and want to discharge to the onsite storm water management system On February 23, 2007, the applicant provided an updated ICPR and the following description: “The model was modified by adding 600 gallons per minute dewatering flow into a node representing the stormwater management system.  The results of this modeling scenario indicate that the existing stormwater management system has sufficient capacity to adequately handle dewatering during a synthetic 25-year, 24-hour storm event.”

My reply: Response acknowledged.  The applicant provided ICPR calculations on February 28, 2007, showing that the addition of produced ground water will not interfere with the required attenuation by the storm water system.

2. The facility’s previous responses to questions #2, 3, 4, have been acknowledged as acceptable. 
This staff assessment is preliminary and is designed to assist in the review of the siting assessment prior to final agency action. The comments provided herein are not the final position of the Department and may be subject to revision pursuant to additional information and further review.

