Amendment Request

Proposed Amendment
The Orlando Utilities Commission (OUC) requests an amendment to the Stanton Energy Center Site Certification Application to install a “Post” sodium hypochlorite feed system at the on site water treatment plant. 

Purpose/Reason for Amendment
The purpose of this amendment is to install a “Post” sodium hypochlorite feed system to the Stanton Energy Center potable water system.  Installation of this system will shift some of its chlorine feed to a “Post” injection point out of the ground storage tank to cut down on the contact time and help maintain the chlorine residual in the potable water system.  

Technical Description of Amendment
Approval of this amendment would allow the addition of the “Post” chlorination system to the potable water system at the Stanton Energy Center.  The current system uses 150 lb chlorine gas cylinders for disinfection.  The raw water is pumped from two upper Floridian Aquifer wells located at the Stanton Energy Center to the on site water treatment plant.  The raw water is pumped to an air stripper to removed hydrogen sulfide gases and then goes to a reactor/softener.  The water then gravity flows to a duel filter before dropping to a clearwell.  The potable water is then pumped from the clearwell to the ground storage tank.  From the ground storage tank the potable water is then pumped to the distribution system throughout the site.  The chlorine gas in a water solution is added at three injection points.  The chlorine is added to the piping leading to the reactor/softener, the piping leading to each of the filters and at the clearwell.  
The “Post” chlorination system will be placed next to the high service pump building next to the ground storage tank west of the on site water treatment plant.  The system will consist of one 1,100 gallon HDLPE tank with chemical feed pumps on a concrete pad covered with a vinyl garden shed.  The new system will be connected by piping from the chemical feed pumps to an injection point on the pipe leading from the ground storage tank to the suction end of the high service pumps.  
Environmental Consequences of Amendment 
OUC anticipates no adverse environmental impacts resulting from the approval and implementation of this amendment.  Installation of the “Post” chlorination system will help maintain the potable water quality as directed by FDEP.
Effect of Amendment on Certification/Conditions of Certification
OUC believes that this proposed amendment makes no change to the applicable Condition of Certification XIII, Potable Water Supply System, and thus is not a modification to the conditions of certification.  The proposed amendment will ensure that the potable water system at Stanton Energy Center will continue to be designed and operated in conformance with the standards contained in Chapter 62-555, F.A.C., as required by the existing conditions of certification.
Submittal Package Included
The submittal package with appropriate application form and supporting documentation that was sent to FDEP-Central District is attached.

