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I. 
CERTIFICATION CONTROL 
A. 
Pursuant to s. 403.501-518, F.S., the Florida Electrical Power Plant Siting Act, this certification is issued to Orlando Utilities Commission, Florida Municipal Power Agency, Kissimmee Utility Authority and Southern-Florida, LLC as joint owner/operators of Curtis H. Stanton Energy Center. Under the control of these Conditions of Certification the OUC will operate a 930 MW (nominal) facility consisting of two coal-fired Units No. 1 and No. 2, and ancillary equipment.  Southern-Florida LLC will construct and operate a 633 MW gas-fired combined cycle facility known as Combined Cycle Unit A. OUC will construct and operate a 300 MW duel fueled (natural/gas/No.2 fuel oil) Combined Cycle unit known as Unit B. These units are located on a 3280-acre site which is located at 5100 South Alafaya Trail, Orlando, Orange County, Florida.  UTM coordinates are: Zone 17; 483.61 km East; 3151.1 km North. Now Condition A.I.A. Scope and Condition A.I.B. Scope with revised language
B. 
The general and specific conditions contained in these Conditions of Certification, unless specifically amended or modified, are binding upon the licensees and shall apply to the construction and operation of the certified facility.  If a conflict should occur between the design criteria of this project and the Conditions of Certification, the Conditions shall prevail unless amended or modified. Now Condition A.I.C. Scope with revised language

II. 
APPLICABLE RULES Now Condition A.II. Applicable Department Rules with revised language
The construction and operation of the certified facility shall be in accordance with all applicable provisions of Florida Statutes and Department and Water Management District rules, including the following regulations: [St. Johns River WMD:  40 C-2, 40C-3, 40C-8, 40-C21 ] [South Florida WMD: 40E-1, 40E-4, 40E-40, 40E-41,] 62-4, 62-17, 62-256, 62-296, 62-297, 62-301, 62-302, 62-531, 62-532, 62-550, 62-555, 62-560, 62-600, 62-601, 62-604, 62-610, 62-620, 62-621, 62-650, 62-699, 62-660, 62-701, 62-762, 62-767, 62-769, and 62-770, Florida Administrative Code (F.A.C.), or their successors as they are renumbered. 

III.
DEFINITIONS Now Condition A. IV. Definitions with revised language
The meaning of terms used herein shall be governed by the definitions contained in Chapter 403, Florida Statutes, and any regulation adopted pursuant thereto.  In the event of any dispute over the meaning of a term used in these general or special conditions which is not defined in such statutes or regulations, such dispute shall be resolved by reference to the most relevant definitions contained in any other state or federal statute or regulation or, in the alternative by the use of the commonly accepted meaning as determined by the Department.  As used herein: 

A. 
"Application" shall mean the Site Certification Application (SCA) for the certified facility, as supplemented. 

B. 
"DEP" or Department shall mean the Florida Department of Environmental Protection. 

C. 
"DHR" shall mean the Florida Department of State, Division of Historical Resources. 

D. 
"Emergency conditions" shall mean urgent circumstances involving potential adverse consequences to human life or property as a result of weather conditions or other calamity, and necessitating new or replacement gas pipeline, transmission lines, or access facilities. 

E.
 “Facility” shall mean the certified electrical power generation facility and all associated structures, including but not limited to:  combustion turbine generators, heat recovery steam generators, duct burners, fossil steam boilers, steam turbine generators, selective catalytic reduction units, transformers, associated transmission lines, substations, fuel and water storage tanks, natural gas delivery metering station, air and water pollution control equipment, storm water control ponds and facilities, cooling towers, and related structures. 

F.
 "Feasible" or "practicable" shall mean reasonably achievable considering a balance of land use impacts, environmental impacts, engineering constraints, and costs. 

G.
 "FFWCC" shall mean the Florida Fish and Wildlife Conservation Commission. 

H. 
"Licensee" means an applicant that has obtained a certification order for the subject project. 

I.
 “NPDES permit” shall mean the federal National Pollutant Discharge Permit System permit issued in accordance with the federal Clean Water Act. 

J.
 "Power plant" shall mean the electric power generating plant and associated structures to be modified or constructed on the certified site, as generally depicted in the Application. 

K. 
"Project" shall mean the electrical power generating facility and all associated facilities. 

L. 
“PSD permit” shall mean the federal Prevention of Significant Deterioration air emissions permit issued in accordance with the federal Clean Air Act. 

M. 
"NWF, SR, SJR, SWF, or SF WMD" shall mean the Northwest Florida, Suwannee River, St. Johns River, Southwest Florida, or South Florida Water Management District. 

N. 
“Title V permit” shall mean the federal permit issued in accordance with Title V of the federal Clean Air Act. 

IV. 
GENERAL CONDITIONS 

A.
Facility Operation 

1. The Licensee shall at all times properly operate and maintain the facility and related appurtenances, and systems of treatment and control that are installed and used to achieve compliance with the conditions of this certification, and are required by Department rules.  This provision includes the operation of backup or auxiliary facilities or similar systems when necessary to achieve compliance with the conditions of the approval and when required by Department rules. Now Condition A. XXIX. Facility Operation
2. In the event of a prolonged [thirty (30) days or more] equipment malfunction or shutdown of pollution control equipment, facility operation may be allowed to resume and continue to take place under an appropriate Department order, provided that the licensee demonstrates that such operation will be in compliance with all applicable ambient air quality standards and PSD increments, water quality standards and rules, solid waste rules, domestic wastewater rules and industrial wastewater rules. During such malfunction or shutdown, the operation of the facility shall comply with all other requirements of this certification and all applicable state and federal emission and effluent standards not affected by the malfunction or shutdown. Now Condition A.VIII. Replacement for Restoration of System Integrity and Emergency Conditions
B.
Records Maintained at the Facility Now Condition A.XXX. Records Maintained at the Facility
1. These Conditions of Certification or a copy thereof shall be kept at the work site of the approved activity. 

2. The licensee shall hold at the facility, or other location designated by this approval, records of all monitoring information, including all calibration and maintenance records and all original strip chart recordings for continuous monitoring instrumentation required by this approval, copies of all reports required by this approval, and records of all data used to complete the application for this approval.  These materials shall be retained at least three (3) years from the date of the sample, measurement, report, or application unless otherwise specified by Department rule.  The licensee shall provide copies of these records to the Department upon request.  If the licensee becomes aware of relevant facts that were not submitted or were incorrect in any report to the Department, such facts or information shall be promptly submitted or corrected. 

C.
Change in Discharge Now Condition A. XXIII. D. Modification of Certification
All discharges or emissions authorized herein shall be consistent with the terms and conditions of this certification. The discharge of any pollutant not identified in the application, or more frequently than, or at a level in excess of that authorized herein, shall constitute a violation of the certification.  Any anticipated facility expansions, production increases, or process modifications which may result in new, different or increased discharges or pollutants, change in fuel, or expansion in steam generating capacity must be reported by submission of a new application for amendment or modification pursuant to Chapter 403.516, F.S. 

D.
Noncompliance Notification Now Condition A. VII. Notification
If, for any reason, the licensee does not comply with or is unable to comply with any limitation specified in this certification, the licensee shall notify the Central District Office of the Department by telephone during the working day that said noncompliance occurs. After normal business hours, the licensee shall report any condition that poses a public health threat to the State Warning Point at telephone number (850) 413-9911 or (850) 413-9912.  The licensee shall confirm this situation to the DEP District Office in writing within seventy-two (72) hours of becoming aware of such conditions and shall supply the following information: 

1. A description of the discharge and cause of noncompliance; and, 
2. The period of noncompliance, including exact dates and times; or, if not corrected, the anticipated time the noncompliance is expected to continue, and, 
3. Steps being taken to reduce, eliminate and prevent recurrence of the non-complying event. 
E. 
Adverse Impact Now Condition A. XXIX. Facility Operation
The licensee shall take all reasonable steps to minimize any adverse impact resulting from noncompliance with any limitation specified in this certification, including such accelerated or additional monitoring as necessary to determine the nature and impact of the non-complying event. 

F.
 Right of Entry Now Condition A. X. Right of Entry
The licensee shall allow authorized Department personnel, including authorized representatives of the Florida Department of Environmental Protection, Water Management Districts, and/or United States Environmental Protection Agency, when applicable, upon presentation of credentials or other documents as may be required by law, and at reasonable times, depending upon the nature of the concern being investigated: 

1.
To enter upon the licensee's premises where an effluent source is located or in which records are required to be kept under the terms and conditions of this permit; and, 

2.
To have access to and copy any records required to be kept under the conditions of this certification; and, 

3.
To inspect and observe the permitted facilities, equipment, practices, or operations regulated or required under these Conditions to determine compliance with the approved plans, specifications and conditions of this certification; and, 

4.
To sample or monitor any substances or parameters at any location necessary to assure compliance with these Conditions or Department rules. 

G. 
Enforcement Now Condition A. XIII. Enforcement
1.
The terms, conditions, requirements, limitations and restrictions set forth in these Conditions of Certification are binding and enforceable pursuant to Sections 403.141, 403.161, 403.514,. Any noncompliance with a Condition of Certification or condition of a federally delegated or approved permit constitutes a violation of chapter 403, F.S., and is grounds for enforcement action, permit termination, permit revocation, or permit revision.  The Licensee is placed on notice that the Department will review this approval periodically and may initiate enforcement action for any violation of these conditions. 

2.
All records, notes, monitoring data and other information relating to the construction or operation of this certified source which are submitted to the Department may be used by the Department as evidence in any enforcement case involving the certified source arising under the Florida Statutes or Department rules, except where such evidence shall only be used to the extent it is consistent with the Florida Rules of Civil Procedure and appropriate evidentiary rules. 

H. 
Revocation or Suspension Now Condition A. XIV. Revocation or Suspension
This certification may be suspended or revoked pursuant to Section 403.512, Florida Statutes, or for violations of any of these Conditions of Certification.  This approval is valid only for the specific processes and operations applied for and indicated in the approved drawings or exhibits.  Any unauthorized deviation from the approved drawings, exhibits, specifications, or conditions of this approval may constitute grounds for revocation and enforcement action by the Department. 

I. 
Civil and Criminal Liability Now Condition A. XV. Regulatory Compliance and Condition A. XVI. Civil and Criminal Liability
1.
This certification does not relieve the licensee from civil or criminal penalties for noncompliance with any conditions of this certification, applicable rules or regulations of the Department, or Chapter 403, Florida Statutes, or regulations thereunder. 

2.
This certification does not relieve the licensee from liability for harm or injury to human health or welfare, animal or plant life, or property caused by the construction or operation of this permitted source, or from penalties therefore; nor does it allow the licensee to cause pollution in contravention of Florida Statutes and Department rules, unless specifically authorized by an order from the Department. 

3.
As provided in Subsections 403.087(7), 403.511, and 403.722(5), F.S., the issuance of this certification does not convey any vested rights or any exclusive privileges.  Neither does it authorize any injury to public or private property or any invasion of personal rights, nor any infringement of federal, state, or local laws or regulations.  This approval is not a waiver of any other Department approval that may be required for other aspects of the total project under federally delegated programs. 

4.
Subject to Section 403.511, Florida Statutes, this certification shall not preclude the institution of any legal action or relieve the licensee from any responsibilities or penalties established pursuant to any other applicable State Statutes or regulations. 

J. 
Property Rights Now Condition A. XV. Regulatory Compliance and A.XVII. Use of State Lands
The issuance of this certification does not convey any property rights in either real or personal property, or any exclusive privileges, nor does it authorize any injury to public or private property or any invasion of personal rights, nor any infringement of Federal, State or local laws or regulations.  The applicant shall obtain title, lease or right of use from the State of Florida, to any sovereign submerged lands utilized by the project. 

K. 
Severability Now Condition A.XII. Severability
The provisions of this certification are severable, and if any provision of this certification, or the application of any provision of this certification to any circumstances, is held invalid, the application of such provision to other circumstances and the remainder of the certification shall not be affected thereby. 


Condition is no longer applicable 
M. 
Procedural Rights Now Condition A.XVIII. Procedural Rights
Except as specified in Chapter 403, F.S., or Chapter 62-17, F.A.C., no term or condition of certification shall be interpreted to preclude the post-certification exercise by the licensee of whatever procedural rights it may have under Chapter 120, F.S., including those related to rule-making proceedings. 

N. 
Modification of Conditions Now Condition A.XXIII. Modification of Certification
The conditions of this certification may be modified in the following manner: 

1.
The licensee shall comply with rules, adopted by the Department subsequent to the issuance of the certification, which prescribe new or stricter criteria to the extent that the rules are applicable to electric power plants.  Except where express variances, exceptions, exemptions, or other relief have been granted, subsequently adopted rules which prescribe new or stricter criteria shall operate as automatic modifications to the certification. 

2.
The licensee may choose to operate in compliance with any rule subsequently adopted by the Department which prescribes criteria more lenient than the criteria required by the terms and conditions in the certification which are not site specific. 

3.
The Siting Board hereby delegates to the Secretary of the Department of Environmental Protection the authority to modify, after notice and opportunity for hearing, any conditions herein which would not otherwise require approval from the Siting Board. 
O. 
Transfer of Certification Now Condition A.XXV. Transfer of Certification
This certification is transferable only upon Department approval in accordance with Section 403.516, F.S., and Rules 62-17.211(3) and 62-730.300, F.A.C., as applicable. The licensee shall be liable for any noncompliance of the approved activity until the transfer is approved by the Department. 

P. 
Safety Now Condition A.XV. Regulatory Compliance
The overall design, layout, and operation of the facilities shall be such as to minimize hazards to humans and the environment.  Security control measures shall be utilized to prevent exposure of the public to hazardous conditions.  The Federal Occupational Safety and Health Standards shall be complied with during construction and operation. 

Q. 
Screening See New Condition B.VIII.B. Screening
The Licensee shall provide screening of the site to the extent feasible through the use of aesthetically acceptable structures, vegetated earthen walls and/or existing or planted vegetation 

R. 
Toxic, Deleterious or Hazardous Materials Now Condition A.XXXI. Water Discharges and XXXII.C. Hazardous Substance Release Notification
1.
The Licensee shall not discharge to surface waters wastes which are acutely toxic, or present in concentrations which are carcinogenic, mutagenic, or teratogenic to human beings or to significant locally occurring wildlife or aquatic species.  The Licensee shall not discharge to ground waters wastes in concentrations which, alone or in combination with other substances, or components of discharges (whether thermal or non-thermal) are carcinogenic, mutagenic, teratogenic, or toxic to human beings (unless specific criteria are established for such components in Section 62-520.420, F.A.C.) or are acutely toxic to indigenous species of significance to the aquatic community within surface waters affected by the ground water at the point of contact with surface waters. 
2.
The licensee shall report all spills of materials having potential to significantly pollute surface or ground waters and which are not confined to a building or similar containment structure, by telephone immediately after discovery of such spill.  The licensee shall submit a written report within forty-eight hours, excluding weekends, from the original notification.  The telephone report shall be submitted by calling the DEP District Office Industrial Wastewater Compliance/Enforcement Section.  After normal business hours, the licensee shall contact the State Warning Point by calling (850) 413-9911 or (850) 413-9912. The written report shall include, but not be limited to, a detailed description of how the spill occurred, the name and chemical make-up (include any MSDS sheets) of the substance, the amount spilled, the time and date of the spill, the name and title of the person who first reported the spill, the size and extent of the spill and surface types (impervious, ground, water bodies, etc.) it impacted, the cleanup procedures used and status of completion, and include a map or aerial photograph showing the extent and paths of the material flow.  Any deviation from this requirement must receive prior approval from the Department. 
S. 
Noise Now Condition B.VIII.A. Local Government Noise
Construction noise shall not exceed noise criteria or any applicable requirements of Orange County. The licensee shall notify area residents in advance of the onset and anticipated duration of the steam blowout of the facility's heat recovery steam generator and steam lines. Such steam blowout shall be conducted between 7:00 A.M. and sunset. 

T. 
Flood Control Protection Now Condition A.IX.C. Flood Control Protection
The plant and associated facilities shall be constructed in such a manner as to comply with the appropriate County flood protection requirements, either by flood proofing or by raising the elevation of the facilities above the 100-year flood level. 

U. 
Historical or Archaeological Finds Now Condition B.VI.B. Department of State – Division of Historical Resources
  If historical or archaeological artifacts, such as Indian canoes, are discovered at any time within the project site, the licensee shall notify the DEP District office and the Bureau of Historic Preservation, Division of Historical Resources, R.A. Gray Building, Tallahassee, Florida 32399, telephone number (850) 487-2073. 

V. 
Endangered and Threatened Species Now Condition B.V. Florida Fish and Wildlife Conservation Commission
Prior to start of construction, the licensee shall survey the certified site for endangered and threatened species of animal and plant life.  Plant species listed as endangered or threatened by the federal government and plant species listed as endangered by the state shall be transplanted to an appropriate area if practicable.  Gopher tortoises and any commensals on the rare or endangered species list shall be relocated after consultation with the FFWCC. A relocation program, as approved by the FFWCC, shall be followed. Entombment of gopher tortoises shall not be allowed. 

 W. 
Dispute Resolution Now Condition A.XI.A. General
If a situation arises in which mutual agreement cannot be reached between the Licensee and an agency exercising its regulatory jurisdiction, then the matter shall be immediately referred to the Division of Administrative Hearings (DOAH) for disposition in accordance with the provisions of Chapter 120, F.S. 

X. 
Laboratories And Quality Assurance Now Condition A.XXVI. Laboratories and Quality Assurance and Condition A. XXX. Records Maintained at the Facility
1.
The licensee shall ensure that all laboratory analytical data submitted to the Department, as required by this Certification, are from a laboratory which has a currently valid and Department approved Comprehensive Quality Assurance Plan (CompQAP) or a CompQAP pending approval for all parameters being reported, as required by Chapter 62-160, F.A.C. 

2.
The licensee shall ensure that all samples required pursuant to this certification are taken by an appropriately trained technician following EPA and Department approved sampling procedures and chain-of-custody requirements in accordance with Rule 62-160, F.A.C.  All chain-of-custody records shall be retained on-site for at least three (3) years and made available to the Department immediately upon request. 

3. 
Records of monitoring information shall include: 

a. 
the date, exact place, and time of sampling or measurements; 

b. 
the person responsible for performing the sampling or measurements; 

c. 
the dates analyses were performed; 

d. 
the person responsible for performing the analyses; 

e. 
the analytical techniques or methods used; and, 

f. 
the results of such analyses. 

Y. 
Procedures For Post-Certification Submittals Now Condition A.XX. Procedures for Post-Certification Submittals 
1. 
Purpose of Submittals: Conditions of Certification which provide for the post-certification submittal of information to DEP or other agencies by the licensee are for the purpose of facilitating monitoring by the Department of the effects arising from the plant facilities.  This monitoring is for DEP to assure, in consultation with other agencies with applicable regulatory jurisdiction, continued compliance with the conditions of certification, without any further agency action. 

2.
Filings: All post-certification submittals of information by the licensee are to be filed with DEP.  Copies of each submittal shall be simultaneously submitted to any other agency indicated in the specific conditions requiring the post-certification submittals. 

3.
Completeness: The DEP shall promptly review each post-certification submittal for completeness. This review shall include consultation with the other agencies receiving the post-certification submittal. For the purposes of this condition, completeness shall mean that the information submitted is both complete and sufficient. If the submittal is found to be incomplete, the licensee shall be so notified.  Failure to issue such a notice within forty-five (45) days after filing of the submittal shall constitute a finding of completeness. 

4.
Interagency Meetings: Within sixty (60) days of the filing of a complete post-certification submittal, DEP may conduct an interagency meeting with other agencies which received copies of the submittal.  The purpose of such an interagency meeting shall be for the agencies with regulatory jurisdiction over the matters addressed in the post-certification submittal to discuss whether reasonable assurance of compliance with the conditions of certification has been provided. Failure of any agency to attend an interagency meeting shall not be grounds for DEP to withhold a determination of compliance with these conditions nor to delay the time frames for review established by these conditions. 

5.
Reasonable Assurance of Compliance:  Within ninety (90) days of the filing of a complete post-certification submittal, or 45 days after a submittal is made by the licensee, or unless another date is specified herein, DEP shall give written notification to the licensee and the agencies to which the post-certification information was submitted of its determination whether there is reasonable assurance of compliance with the conditions of certification.  If it is determined that reasonable assurance has not been provided, the licensee shall be notified with particularity and possible corrective measures suggested. Failure to notify the licensee in writing within ninety (90) days of receipt of a complete post-certification submittal shall constitute a determination of reasonable assurance of compliance. 

V. 
CONSTRUCTION 

A.
Standards and Review of Plans Now Condition A.XX. Procedures for Post-Certification Submittals
1. 
All construction at the facility shall be pursuant to the design standards presented in the application or amended application and the standards or plans and drawings submitted and signed by an engineer registered in the state of Florida. Specific Central DEP District Office acceptance of plans will be required based upon a determination of consistency with approved design concepts, regulations, and these conditions prior to initiation of construction of any: industrial waste treatment facility; domestic waste treatment facility; potable water treatment and supply system; ground water monitoring system, storm water runoff system; solid waste disposal area; and hazardous or toxic handling facility or area.  The Licensee shall present specific plans for these facilities for review by the DEP Central District Office at least ninety (90) days prior to construction of those portions of the facility for which the plans are then being submitted, unless other time limits are specified in the following conditions herein.  Review and approval or disapproval shall be accomplished in accordance with Chapter 120, F.S., or these conditions of certification as applicable.  The licensee shall not proceed with construction of any wastewater treatment and disposal system without a written authorization from the Department. Now Condition A.XX. Procedures for Post-Certification Submittals
2.
The Department must be notified in writing and prior written approval obtained for any material change, modification, or revision to be made to the project during construction which is in conflict with these conditions of certification.  If there is any material change, modification, or revision made to a project approved by the Department without this prior written approval, the project will be considered to have been constructed without departmental approval, the construction will not be cleared for service, and the construction will be considered a violation of the conditions of certification. Now Condition A.XX. Procedures for Post-Certification Submittals




2.
Any open burning in connection with initial land clearing shall be in accordance with Chapter 62-256, F.A.C., Chapter 5I-2, F.A.C., Uniform Fire Code Section 33.101 Addendum, and any other applicable County regulation.  Any burning of construction-generated material, after initial land clearing that is allowed to be burned in accordance with Chapter 62-256, F.A.C., shall be reviewed by the DEP Central District office in conjunction with the Division of Forestry and any other county regulations that may apply. Burning shall not occur if not approved by the appropriate agency or if the Department or the Division of Forestry has issued a ban on burning due to fire safety conditions or due to air pollution conditions. Now Condition A.IX.B. Open Burning
 This condition is no longer applicable
4.
Solid wastes resulting from construction shall be disposed of in accordance with the applicable regulations of Chapter 62-701, F.A.C. Now Condition A.XXXIII.A, Solid Waste Now Condition A.XXXII.A. Solid Waste
5.
Construction noise shall not exceed noise criteria or any applicable requirements of Orange County. To mitigate the effects of noise produced by the steam blowout of steam boiler tubes, the licensee shall conduct public awareness campaigns prior to such activities to forewarn the public of the estimated time and duration of the noise. Now Condition B.VIII.A. Noise
6.
The licensee shall employ proper odor and dust control techniques to minimize odor and fugitive dust emissions. The applicant shall employ control techniques sufficient to prevent nuisance conditions which interfere with enjoyment of residents of adjoining property. Covered under A.V.A. Air with revised language
7.
Directly associated transmission lines from the facility electric switchyard to existing transmission lines shall be maintained in accordance with the application and the appropriate state and federal regulations concerning use of herbicides. The Licensee shall notify the Department of the type of herbicides to be used at least 60 days prior to their first use. Now B.VII. Department of Agriculture and Consumer Services
8.
The licensee shall develop the site so as to retain the buffer of natural vegetation as described in the application and in Condition IV.Q. Screening. Now Condition B.VIII.B. Screening
Dewatering operations during construction shall be carried out in accordance with Rule 62-621.300(2), F.A.C. Now Condition XXVII. Environmental Resources

 This Condition is no longer applicable.
D. 
Reporting Now Condition B.I.G. Reporting
Notice of commencement of construction shall be submitted to the Siting Coordination Office and the DEP Central District Office within fifteen (15) days of initiation. Starting three (3) months after construction commences, a quarterly construction status report shall be submitted to the DEP Central District Office.  The report shall be a short narrative describing the progress of construction. 

E. 
Pond Perimeter Berms Now Condition B.I.K. Pond Perimeter Berms
Construction of the water storage pond perimeter berms shall be in conformance with the provisions of Chapter 62-672, F.A.C, regarding earthen dams, and should be inspected regularly by a licensed engineer. 



G. 
Stormwater Review Now Condition A.XXVII. Environmental Resources
1.
At least ninety days prior to the commencement of construction, the licensee shall provide all information necessary for a complete Environmental Resource Permit application including the engineering drawings and supporting documentation necessary to demonstrate that the stormwater runoff from the proposed project will be treated and attenuated in accordance with Rules 40C-4, 40C-41 and 40C-42, F.A.C.  The drawings and documentation shall be signed, sealed and dated by a professional engineer registered in the State of Florida. 

2.
Prior to the commencement of construction, the Department shall conduct a timely review of the submitted information and request the correction of any errors and omissions and any additional information necessary to complete the application.  This shall be done in accordance with timeframes established in Chapter 120.60, F.S. and Rule 62-4.055, F.A.C. 

3.
The Department shall notify the licensee in writing that the application is complete upon review of all requested information and the correction of any errors or omissions.  Construction shall not begin until the Department has provided such written notification. 

4.
Turbidity and sediments must be controlled to prevent violations of water quality pursuant to Rule 62-302.500, 62-302 .530(70) and 62-4.242 Florida Administrative Code (FAC). Best Management Practices, as specified in the Florida Stormwater, Erosion and Sedimentation Control Inspectors Manual, shall be installed and maintained at all locations where the possibility of transferring suspended solids into wetlands and/or surface waters due to the permitted activity. If site-specific conditions require additional measures, then the Applicant shall implement them as necessary to prevent adverse impacts to wetlands and/or surface waters. 

5.
The existing ambient water quality within Outstanding Florida Waters shall not be lowered as a result of the proposed activity, except as authorized by the FDEP under 62-4.242(2) FAC. 

This Condition is no longer applicable.
VI. 
AIR  Now in Condition A.V.A. Air
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2. 
3. 
4. 
5. 
6. 
7. 
8. 
9. 
I. 
State Water Quality Standards Now Condition XXVII. Environmental Resources with revised language
The project shall comply with applicable state water quality standards, including: 

1. 
62-302.500 - minimum criteria for all surface waters at all places and at all times, 

2. 
62-302.500 - Surface waters: general criteria,  

3.
62-302.400 - Class III Waters - Recreation, Propagation and maintenance of a healthy, well balanced population of Fish and Wildlife, and 

4.
62-302.530(70) - Turbidity shall not exceed 29 Nephelometric Turbidity Units above background. 
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VIII. 
ELECTRIC AND MAGNETIC FIELDS Now Condition A.IX.F, Electric and Magnetic Fields (EMF)
The associated transmission lines shall comply with the requirements of Ch. 62.814, F.A.C. 

IX. 
COOLING TOWER Now Condition B.I.D. Cooling Tower with revised language
A. 
Makeup Water Constituency 

The CHSEC shall utilize treated sewage effluent, treated wastewater, onsite re-use water, landfill stormwater/leachate, stormwater runoff, or direct precipitation to the makeup water supply storage pond, as cooling tower makeup water.  The effluent shall have received prior to use in the tower sufficient treatment from the source of cooling water, “a sewage treatment plant”, but as a minimum, secondary treatment, as well as treatment described in Condition IX.B. below. Use of waters other than treated sewage effluent, or storm water, i.e., higher quality potable waters, or lower quality less-than-secondarily-treated sewage effluent, will require a modification of conditions pursuant to condition IV.N.3
. 

B. 
Chlorination 
Treated sewage effluent used as cooling water makeup shall be treated to maintain a 1.0 mg/liter free chlorine residual for a 15 minute contact time, or alternately a demonstration that a viral concentration of less than one PFU per 25 gallons can be achieved at lower levels of chlorination. Chlorine levels shall be monitored continuously at the sewage treatment plants. 

 C. 
Special Studies 
Upon satisfactory demonstration to the Department that the number of viruses entering the towers in the effluent makeup can be reduced to an undetectable level with the use of a lesser amount of chlorination or alternative treatment, the above requirement may be altered.  This demonstration may occur through performance of special studies approved by the Department.  Alteration of the chlorination requirements must still insure adequate treatment for the control of bacteria or viruses in the cooling water. 

X. 
WATER DISCHARGES Now Condition B.I.A Water Discharges
 

























 

D. 
Water Monitoring Program 

The licensee shall monitor and report to the Department the listed parameters on the basis specified herein.  The methods and procedures utilized shall receive written approval by the Department. The monitoring program may be reviewed annually by the Department, and a determination may be made as to the necessity and extent of continuation, and may be modified in accordance with Condition No. 1V.N. 


1.
Chemical Monitoring    
The following parameters shall be monitored during operation as 

shown, commencing with the start of commercial operation of CHSEC and reported quarterly to the Department’s Central District Office: 

	Parameter 
	Location 
	Sample Type 
	Frequency 

	Flow, groundwater 
	Wellfield Pipeline 
	Pump Logs 
	Continuous 

	Flow, Cooling Water Makeup 
	Intake 
	Pump Logs 
	Daily 

	TSS 
	Sewage and Treatment Facility 
	8 Hour Composite 
	Monthly 

	Chlorine 
	CHSES Sewage Treatment Plant 
	Grab 
	Weekly 




















 

XI. 
GROUNDWATER Now Condition B.I.B Groundwater














	
	

	
	

	
	

	
	

	
	



E. 
Shallow Aquifer Monitoring Wells 

After consultation with the DEP and SJRWMD, OUC shall install a monitoring well network to adequately monitor groundwater quality horizontally and vertically from the ground to the bottom of the Hawthorne Formation.  Groundwater levels and flow directions will be determined twice a year (May and September) at the site through the preparation of seasonal piezometric contour maps. From these maps, the water quality monitoring well network will be located.  Monitoring well locations and designs shall be submitted to the Department and SJRWMD for review and approval.  Approval or disapproval of the locations and design shall be granted within 60 days.  Monitoring wells of adequate design and number shall be installed up gradient and down gradient from each solid waste disposal area, each liquid waste pond and each coal pile storage area. An additional monitoring well will be placed immediately down gradient of the first section of each solid waste landfill to be utilized. The water samples collected from each of the monitor wells shall be collected immediately after removal by pumping of a quantity of water equal to two casing volumes.  The water quality analyses shall be performed monthly during the year prior to commercial operation and quarterly thereafter. Results shall be submitted to the Department and the SJRWMD by the fifteenth (15th) day of the month following the month during which such analyses were performed. Testing for the following constituents is required: 

TDS Zinc Conductance Copper PH Nickel Sulfate Selenium Color Arsenic Nitrate Beryllium Chloride Mercury Iron Lead 

Aluminum Gross Alpha, Ra226 (when Gross-

Alpha activity exceed 15 pCi/1 

Cadmium Total Phosphate 

Silver Calcium 

Manganese Magnesium 

Barium Potassium 

Molybdenum Sodium 

   Conductivity shall be monitored in wells around all lined ponds. 

F. 
Leachate 


1. 
Zone of Discharge 

Leachate from the combustion waste landfills, coal storage piles, wastewater ponds, or storage ponds shall not contaminate waters of the State (including both surface and groundwater) in excess of the limitations of Chapter 62-302, or the Primary and Secondary Drinking Water parameters included in Chapter 62-550, F.A.C., beyond the boundary of separate and individual zones of discharge extending 50 feet below the ground surface and 100 feet from the edge of each individual pile or pond, except as provided in Condition XXII. The zone of discharge is defined in chapter 62-520., F.A.C.


 2. 
Corrective Action 

   When the groundwater monitoring system shows a violation of the groundwater quality standards of Chapter 62-550, F.A.C., from this facility the appropriate ponds, combustion waste landfill, or coal pile shall be bottom sealed, relocated, fixed or the operation of the affected facility shall be altered in such a manner as to assure the Department that no violation of the groundwater standards will occur beyond the boundary of the zone of discharge. In addition, contaminated leachates shall be removed from ground waters. 




XII. 
SOLID WASTES 

Solid wastes resulting from construction or operation shall be disposed of in accordance with the applicable regulations of Chapter 62-701, F.A.C.  The licensee shall submit a program for approval outlining the methods to be used in handling and disposal of solid wastes. Such a program shall indicate at the least methods for erosion control, covering, vegetation, and quality control. Now Condition B.I.C Solid Wastes
Open burning in connection with land clearing shall be in accordance with Chapters 62-256 and 5I-2, F.A.C. No additional permits shall be required, but the Orange County Pollution Control Department shall be notified prior to burning.  Open burning shall not occur if the Division of Forestry has issued a ban on burning due to fire hazard conditions. Now Condition B.VIII.F. Open Burning 
XIII.
 POTABLE WATER SUPPLY SYSTEM Now Condition B.I.E Potable Water Supply System
The potable water supply system shall be designed and operated in conformance with Chapter 62-555, F.A.C.  Information as required in 62-4 and 62-555, F.A.C. shall be submitted to the Department prior to construction and operation.  The operator of the potable water supply system shall be certified in accordance with Chapters 62-555.350,62-602.400, and 62-699, F.A.C. 

XIV. 
TRANSFORMER AND ELECTRIC SWITCHING GEAR Now Condition B.I.H Transformer and Switching Gear 
The foundations for transformers, capacitors, and switching gear necessary to connect any CHSEC Unit to existing transmission and distribution system shall be constructed in such a manner as to allow complete collection and recovery of any spills or leakage of oily, toxic, or hazardous substances. 

XV. 
CONSTRUCTION IN WATERS OF THE STATE Now Condition A.XVII. Use of State Lands with revised language
A. 
No construction on sovereign submerged lands shall commence without obtaining lease, easement or title from the Department and/or Trustees of the Internal Improvement Trust Fund. 

B. 
Construction of pilings, railroad right-of-way, culverts, access roads, pipelines, and transmission towers shall be done in a manner to minimize turbidity.  Turbidity screens should be used to prevent turbidity in excess of 29 NTU’s above background beyond 40 meters from the excavation, right-of-way, pile driving, or construction site. 

All spoil from construction of the CHSEC and related facilities shall be trucked to an upland disposal site of sufficient capacity to retain all material. 


















































XVII. 
SOLID WASTE LANDFILL Now Condition B.I.F. Solid Waste Landfill.  Revised proposed language in Modification L document

A. 
The proposed solid waste landfill area shall be monitored and studied pursuant to an adequately detailed groundwater testing and monitoring program as defined in Condition IV, D. and E. The results of this detailed groundwater testing and monitoring program will be used by the Department in determining whether OUC shall affirmatively demonstrate that Florida Water Criteria (Chapter 62-550, F.A.C.) will not be violated. 

B. 
Before construction of the solid waste landfill or any expansion thereof commences, Karst features interfering with the hydrogeological integrity of the site in the vicinity of the solid waste landfill shall be adequately stabilized both physically and hydraulically against, respectively, collapse and unusual downward transport of groundwater. 

C. 
OUC shall select and adopt one or more of the following mitigative measures for controlling water quality beneath the solid waste landfill: 

1.
Use of an adequate chemical fixation process on the solid wastes to achieve a uniform layer at least 18 inches in thickness across the cell with a permeability of 1 x 10-7cm/sec or less. 

2.
Use of an adequate chemical fixation process on the solid wastes to achieve solid waste permeability of 5 x 10-6cm/sec or less. The top of each completed cell shall be constructed with a slope of 0.75% and an effort will be made to decrease the permeability of the top layer of fixed FGD material to less than 5 x 10-6 cm/sec. 

D. 
Ninety days prior to operation of Unit 1, OUC shall submit a program demonstrating how the fixed FGD waste landfill permeability will be maintained at or below a level of 5 x 10-6cm/sec. The DEP will indicate its approval or disapproval of the program within 60 days. OUC shall implement an approved program.
E. 
OUC shall adopt in addition all of the following mitigative measures for further controlling water quality beneath the solid waste landfill: 
1.
Use of adequate ramp-slopes over combustion waste storage cells and an adequate perimeter toe ditch and interceptor ditch system for controlling and concentrating rain runoff within the solid waste landfill area. 

2.
Use of adequate and systematic measures for compacting all solid wastes as they are emplaced within the landfill. 

3.
Maintenance of a soil cover and a viable community of grasses, which would eventually extend over the entire solid waste landfill area. 

F. 
Prior to the commencement of operation of solid waste disposal areas or expansion thereof, the following shall be submitted to the Department and the St. Johns River District Manager for review and approval consistent with other conditions of this certification: 

1. 
Plot Plan - should be drawn on a scale not greater than 200 ft. to the inch showing the following: 

a. 
Dimensions and legal description of the site 

b. 
Location and depth corrected to MSL of soil borings 

c. 
Proposed trenching plan 

d. 
Cover stockpiles 
e. 
Fencing or other measures to restrict access 
f. 
Cross sections showing both original and proposed fill elevation 
g. 
Location, depth corrected to MSL, and construction details of monitoring wells or ditch monitoring points 

2. 
Design Drawings and Maps - may be combined with plot plan and should be drawn on a scale no greater than 200 ft. to the inch showing the following: 

a. 
Topographic map with five foot contour intervals 
b. 
Proposed fill areas 
c. 
Borrow area 
d. 
Access roads 
e. 
Grades required for proper drainage 
f. 
Typical cross sections of disposal site including lifts, borrow areas and drainage controls 
g. Special drainage devices 
3. 
Soil map, Interpretive Guide Sheets and a report giving the suitability of the site for such an operation. 
4. 
Operation plans to direct and control the use of the site. 

5.
An indication by discussion or drawings or both of how the site is designed to meet water quality standards of Chapter 62-302 and 62-550, F.A.C, at the waste site boundary or the boundary of the zone of discharge.  Adequate indications above would include discussion of each mitigative water quality control measure that would be employed, including but not limited to: liners, chemical fixation process, compaction, under drains and chemical treatment facilities, impermeable clay caps, soil and grass communities. 

Based on the Department’s reviews of the above, additions to or modifications of the overall monitoring program may be required for monitoring of runoff, groundwaters, and surface waters which may be affected by the various land filling operations. 

The Department shall indicate its approval or disapproval of the submitted plans, drawings, maps, analyses and contingency plans within 60 days. 

XVIII. TRANSMISSION LINES, ACCESS ROAD, NATURAL GAS PIPELINE AND RAIL SPUR Now Condition B.I.I Transmission Lines, Access Road, Natural Gas Pipeline and Rail Spur










B. 
Other Construction Activities
 

1.
Maintenance roads under control of the licensee shall be planted with native species to prevent erosion and subsequent water quality degradation where drainage from such roads would impact waters of the State significantly. 
2.
Good environmental practices such as described in Environmental Criteria for Electric Transmission Systems as published by the U.S. Department of Interior and the U.S. Department of Agriculture shall be followed to the extent practicable. 
3.
Compliance with the most recent version of the National Electric Safety Code adopted by the Public Service Commission is required. 
4.
Fences running parallel to the transmission line which may become conductive shall be grounded at appropriate intervals; fences running perpendicular to the line shall be grounded at the edge of the right-of-way. 
5.
Field reconnaissance of rare and endangered species shall be performed in order to minimize impacts on these species. 
6.
Open burning in connection with land clearing shall be in accordance with the applicable rules of the Department of Agriculture and Consumer Services. No additional permits shall be required, but the Orange County Pollution Control Board shall be notified prior to burning.  Open burning shall not occur if the Division of Forestry has issued a ban on burning due to fire hazard conditions. Now Condition 
 C. 
Maintenance 
1.
Vegetative clearing operations for maintenance purposes may be carried out within the ROW corridor..   Selective clearing of vegetation is preferred over clearing and grubbing or clear cutting. 
2.
If chemicals or herbicides are to be used for vegetation control, the name, type, proposed use, locations, and manner of application shall be provided to the Department prior to their application for assessment of compliance with applicable regulations
.  Now Condition B.VII. Department of Agriculture and Consumer Services

D. 
Archaeological Sites Now Condition B.VI.A. Department of State – Division of Historical Resources
Any archaeological sites discovered during construction of the transmission lines, access roads or rail spurs shall be disturbed as little as possible and such discovery shall be communicated to the Department of State, Division of Historical Resources (DHR). Potentially affected areas will be surveyed, and if a significant site is located, the site shall be avoided, protected, or excavated as directed by DHR. 




F. 
Emergency Reporting Now Condition A.VIII. Replacement for Restoration


Emergency replacement of previously constructed right-of-way or transmission lines shall not be considered a modification pursuant to Section 403.516, F.S. A verbal report of the emergency shall be made to the Department as soon as possible. Within fourteen (14) calendar days after correction of the emergency, a report to the Department shall be made outlining the details of the emergency and the steps taken for its temporary relief. The report shall be a written description of all of the work performed and shall set forth any pollution control measures or mitigative measures which were utilized or are being utilized to prevent pollution of waters, harm to sensitive areas or alteration of archaeological or historical resources. 


















XIX. 
FLOOD CONTROL PROTECTION Now Condition B.VIII.C Flood Control Protection
The plant and associated facilities shall be constructed in such a manner as to comply with the Orange County flood protection requirements. 

XX. 
RAILROAD SPUR LINE 

Modifications to the railroad spur line proposal as presented in the Site Certification Application would require that the modifications be reviewed by the South Florida Water Management District’s staff for concurrence, and approved by the Secretary. The condition is covered under A.XXIII Modification of Certification 
XXI. 
RED COCKADED WOODPECKER Now Condition B.V.F. Red Cockaded Woodpecker
A. 
Implementation Of Red Cockaded Woodpecker Management Plan 

The management plan for the Red-Cockaded Woodpecker shall be implemented for the life of the facility and is incorporated into these Conditions of Certification as Appendix 6. 

B. 
Red-Cockaded Woodpecker Management Area Identification 

All lands depicted in the Red-Cockaded Woodpecker Management Plan, Figure 4-2, except for the area specifically identified as "construction impact of proposed generating Units 1, 2, 3, and 4" constitute the red-cockaded woodpecker management area subject to the Management Plan. 

C. 
Use And Limitations Of The Red-Cockaded Woodpecker Management Area 

With regard to the red-cockaded woodpecker management area, in addition to Condition XXI.B., above: 

1.
OUC may conduct activities within the red-cockaded woodpecker management area which are provided for in the Siting Board’s certification orders for Units 1 and 2, including without limitation the execution of habitat restoration, enhancement, and creation required as mitigation. 
2.
OUC may conduct management, including maintenance in their existing configuration and condition, of existing unpaved private roads utilized by OUC, maintenance of existing water and sewer lines, of existing transmission lines and substation, and other maintenance and management activities which are consistent with its purposes, within the red-cockaded woodpecker management area. 
3.
OUC shall take appropriate action to manage the red-cockaded woodpecker management area to achieve the purposes required by Condition XXI.B., above, with regard to the red-cockaded woodpecker, and in general to preserve the natural conditions of the area, including other protected species of native wildlife, vegetation, wetlands, and particularly the tributaries and headwaters of the Econlockhatchee River. OUC may act to implement the red-cockaded woodpecker management plan, to monitor its effectiveness, and to react to fire, flood, or other unforeseeable natural or manmade disturbances. Any reports generated by OUC concerning activities within or management of the red-cockaded woodpecker management area shall be provided to the Florida Fish and Wildlife Commission.

4.
OUC shall allow only those activities of others within the red-cockaded woodpecker management area which are consistent with its management in a natural state. Such activities shall be limited to environmental restoration, scientific research, habitat management (such as controlled burning) and nature study. 
5.
Unless specifically authorized by an order of the Siting Board, dredging, filling, construction of buildings, road-ways, dumping of debris, excavation, and clearing of native vegetation shall be prohibited in the area defined by Condition XXI.B., above. The provisions of Sections 403.516(1)(a) and (b), F.S., notwithstanding, OUC agrees that any activity prohibited in this paragraph within the area described in the red-cockaded woodpecker management area shall be authorized only by affirmative vote of the Siting Board. 
6.
OUC hereby stipulates as a factual matter, which shall be binding on it, and all of its officers, agents, attorneys, and employees, that the "alternate access road" authorized by this supplemental certification completes the necessary roadway access for Units 1 and 2, to allow the full development thereof.  Any additional access for electric power generation, and any additional facilities necessary for the construction of Units 3 and 4 will be the subject of a comprehensive Supplemental Certification Application or applications for Units 3 and 4. 
7.
If OUC determines to pursue a modification of its certification with regard to the easement recorded December 30, 1987, at ORB 3946, Page 3187, Orange County, Florida, it shall do so as a ministerial act only and shall not actively utilize its resources, funds or personnel to support such an application. 





XXIII. FISH AND WILDLIFE MANAGEMENT Now Condition B.V. Florida Fish and Wildlife Conservation Commission

XXIV. COAL PILE Now Condition B.I.J. Coal Pile with revised language
The coal pile shall be lined with a material with a permeability not greater than 1 x 10-7 cm/sec. or the leachate shall be controlled to prevent violation of water quality criteria beyond the zone of discharge. 

XXV. FISH AND WILDLIFE CONSERVATION COMMISSION Now Condition B.V. Florida Fish and Wildlife Conservation Commission
 







































































































XXIX. ST. JOHNS RIVER WATER MANAGEMENT DISTRICT Now Condition B.III. St. Johns River Water Management District
A. 
Water Shortages 

Nothing in this certification shall be construed to limit the authority of the SJRWMD to declare a water shortage and issue orders pursuant to Section 373.175, Florida Statutes or to formulate a plan for implementation during periods of water shortage, pursuant to Section 373.246, Florida Statutes. In the event of a water shortage, as declared by the SJRWMD Governing Board, the Licensees must adhere to reductions in water withdrawals as specified by the SJRWMD. Pursuant to Section 403.516, Florida Statutes, in the event of a water shortage as declared by the SJRWMD governing board, DEP may seek a modification of the terms and conditions of this certification to implement the water shortage declaration and the licensees must adhere to reductions in water withdrawals as specified by SJRWMD. 

B. 
Well Construction, Modification, Or Abandonment 

Prior to the construction, modification, or abandonment of an on-site well, the Licensees must submit a completed application form for a Water Well Construction Permit to DEP and SJRWMD.  All construction, modification, or abandonment of water wells must be conducted under the supervision of a licensed water well contractor and must be performed in accordance with Chapter 40C-3, F.A.C.  Construction of a well will require modification of the certification when such construction is other than that specified and described in the Site Certification Application.  Prior to modification or abandonment of a well, the Licensees must file an amendment to the site certification application with DEP and SJRWMD.  Upon completion of the construction, modification or abandonment of each well, the Licensees must submit to SJRWMD and DEP a completion report for the well. [Paragraphs 16.0(c); 10.3(b)(d)(h)(j), A.H.] 

C. 
Well Maintenance 
Leaking or inoperative well casings, valves, or controls must be repaired or replaced as required to put the system back in an operative condition acceptable to the SJRWMD. Failure to make such repairs will be cause for deeming the well abandoned in accordance with Part II of chapter 373, F.S., and chapter 40C-3, F.A.C., and the rules promulgated thereunder. [Paragraphs 16.0(d); 10,3(b)(d)(h)(i), A.H.] 

D. 
Mitigation Of Withdrawal Impacts On Existing Legal Users 
Licensees must mitigate any adverse impact caused by withdrawals permitted herein on legal uses of water existing at the time of the initial application for the Stanton Energy Center. DEP has the right to curtail permitted withdrawal rates or water allocations if the withdrawals of water cause an adverse impact on legal uses of water which existed at the time of application.  Adverse impacts are exemplified by but not limited to: 

1.
Reduction of water levels in an adjacent surface water body resulting in a significant impairment of the use of water in that water body. 
2.
Saline water intrusion or introduction of pollutants into the water supply of an adjacent water use resulting in a significant reduction of water quality; and 
3.
Change in water quality resulting in either impairment or loss of use of a well or water body. [Paragraphs 9.2; 10.3(b)(d)(h)(j), A.H.] 

E. 
Mitigation Of Impacts On Adjacent Land Uses 
Licensee must mitigate any adverse impact caused by withdrawals permitted herein on an adjacent land use which existed at the time of Supplemental Site Certification Application for Stanton 2 and any subsequent unit. DEP has the right to curtail permitted withdrawal rates or water allocations unless the impacts can be mitigated by licensee. Adverse impacts are exemplified by, but not limited to: 

1.
Significant reduction in water levels in an adjacent surface water body; 

2.
Significant potential for land collapse or subsidence off-site caused by a reduction in water levels; or 

3.
Damage to crops, wetlands and other types of off-site vegetation. [Paragraphs 9.4.3; 10.3(b)(d)(g)(h)(i), A.H.] 

F.
 Identification Tags 

A SJRWMD-issued identification tag must be prominently displayed at each withdrawal site by permanently affixing such tag to the pump, head-gate, valve or other withdrawal facility as provided by Section 40C-2.401, Florida Administrative Code. Licensee must notify the SJRWMD in the event that a replacement tag is needed 
[Paragraphs 16.0(h); 10.3(b)(d)(g)(h)(i), A.H.] 

G. 
Submittals 
All submittals made to demonstrate compliance with the consumptive use and water well construction conditions of this certification must have the certification number plainly labeled on the submittal. [Paragraphs 10.3(a)-(j)(i), A.H.] 

H. 
Maximum Annual Withdrawals 
Maximum annual groundwater withdrawals from the Floridan aquifer for demineralizer/steam cycle makeup, general service water, heat recovery steam generation, wash-down, injection and power augmentation, and domestic uses combined must not exceed 321.2 million gallons per year. [Paragraphs 10.3.;(a)(b)(c)(e)(f)(g), A.H.] 

I. 
Maximum Daily Withdrawals 
  Maximum daily groundwater withdrawals from the Floridan aquifer for demineralizer/steam cycle makeup, general service water, heat recovery steam generation, wash-down, injection and power augmentation, and domestic uses combined must not exceed 2.00 million gallons per day. 

[Paragraphs 10.3;(a)(b)(c)(e)(f)(g), A.H.] 

J.
 Limitation On Uses Of Water 
1.
The maximum annual ground water withdrawals from the Floridan Aquifer for fire protection (essential use) must not exceed 2.48 million gallons per day. [Paragraphs 10,3(a)(b)(c)(f)(g)(h)(i), A.H.] 
2.
The annual allocation of reclaimed water from the Orange County Easterly Water Reclamation Facility and surface/stormwater from the Orange County Landfill for power plant cooling and other power plant uses is: 

4,745.0 million gallons in 2008 and 2009; 

5,365.5 million gallons in 2010 and beyond. 


Licensees must use available surface water to the maximum extent possible prior to using reclaimed water. [Paragraphs 10.3(a)(b)(c)(f)(k), A.H.] 

3.
Withdrawals from the Floridan aquifer wells must not be used directly for cooling tower make-up water. 


4.
If unacceptable saline water intrusion occurs at the on-site wellfield as a result of the withdrawal authorized by this certification, DEP will revoke the allocation of ground water in this certification in whole or in part to curtail or abate the impact caused by the saline water intrusion. [Paragraphs 10,3(b)(c)(d)(g)(h)(i), A.H.] 



K. 
Dewatering 

All withdrawals from the surficial aquifer for dewatering to facilitate construction of Unit A must be retained within the Unit A stormwater detention pond. 
L. 
Well Water Quality Sampling 
Water quality samples must be taken in April and October of each year from each production well. The samples must be analyzed for the following parameters: 

Calcium Chloride Magnesium Sulfate Sodium Carbonate Potassium Bi-Carbonate (or alkalinity if pH is 6.9 or lower) 

All major ion analyses must be checked for anion-cation balance and must balance within 5% prior to submission. It is recommended that duplicates be taken to allow for laboratory problems or loss. The sample analyses must be submitted to the SJRWMD by May 15 and November 15 of each year. Prior to sample collection, a minimum of 3-5 casing volumes must be removed from each well. 
M. 
Water Treatment Plant Reports 
By January 31 of each year, OUC, et al., must submit to the SJRWMD copies of the previous year (12 months) DEP monthly water treatment plant operating report data showing total flow from the 2 Floridan wells going to the potable water treatment plant on-site. The project name and certification number must be attached to all reports. 

N. 
Well Water Flow Monitoring 
1.
OUC, et al., must maintain the continuous recorder on the Floridan aquifer monitor well. Copies of the previous year (12 months) recorder charts must be forwarded to the SJRWMD on a yearly basis. The charts must be submitted by January 31 of each year. Well Nos. 1 and 2 and all reclaimed water and stormwater delivery points must have in-line totalizing flow meters installed prior to use (not including well development). The totalizing flow meters must maintain 95% accuracy, be verifiable, and be installed according to manufacturer specifications.  Documentation of proper installation of flow meters (e.g. photograph) shall be submitted to the SJRWMD within 30 days of meter placement. A site visit by SJRWMD staff can also fulfill this documentation requirement. 

2.
Total withdrawal from well nos. 1 and 2 and all reclaimed water and stormwater delivery points, as listed on the application, must be recorded continuously, totaled monthly, and reported to DEP and SJRWMD at least every six months using SJRWMD Form No. EN-50.  The reporting dates each year will be as follows: 

Reporting Period Report Due Date January - June July 31 July - December January 31 

[Paragraphs 6.7.1.1; 6.7.1.2; 6.7.1.8.1, 10.3(a)(b), A.H.] 

O.
Conservation Plans 
OUC, et al., must implement the conservation plan submitted to the SJRWMD in accordance with the schedule contained therein.
P. 
Maintenance And Calibration Of Flow Meters 
1. 
The Licensees must maintain the meters.  In case of failure or breakdown of any meter, DEP and SJRWMD must be notified in writing within 5 days of its discovery. A defective meter must be repaired or replaced within 30 days of its discovery. 

[Paragraphs 6.7.1; 10.3(a)(b), A.H.] 
2.
OUC, et al., must have all flow meter (s) calibrated once every 3 years within 30 days of the anniversary date of certification issuance, and recalibrated if the difference between the actual flow and the meter reading is greater than 5%. SJRWMD form EN-51 must be submitted to DEP and SJRWMD within 10 days of the inspection/calibration. [Paragraphs6.7.1; 6.7.1.8.1; 10.3(a)(b), A.H.] 






R. 
Use of Lowest Quality Water 
The lowest quality water source, such as reclaimed water and surface/storm water, must be used when deemed feasible pursuant to District rules and applicable state law. [Paragraphs 10.3(f)(g), A.H.] 








































CC. 
Right to Enter 
St. Johns River Water Management District (SJRWMD) and DEP authorized staff, upon proper identification, will have permission to enter, inspect and observe permitted and related facilities in order to determine compliance with the approved plans, specifications and conditions of this certification. [Paragraphs 16.0(a); 10.3(a)-(h)(j), A.H.] 
DD.
Post Certification Information Submittals 

Information submitted to the SJRWMD subsequent to Certification, in compliance with the conditions of this Certification, shall be for the purpose of the SJRWMD determining the Licensee’s compliance with the Certification conditions and the non-procedural criteria contained in Chapter 40C-2, F.A.C., as applicable, prior to the commencement of the subject construction, operation and/or maintenance activity covered thereunder. 

XXX. FLORIDA DEPARTMENT OF TRANSPORTATION Now Condition B.II. Department of Transportation






















































D. 
Best Management Practices 

Traffic control will be maintained during plant construction and maintenance in compliance with the standards contained in the Manual of Uniform Traffic Control Devices; Rule Chapter 14-94, Statewide Minimum Level of Service Standards, Florida Administrative Code; Florida Department of Transportation's Roadway and Traffic Design Standards; Florida Department of Transportation's Standard Specifications for Road and Bridge Construction; and the Department's Utility Accommodation Manual, whichever is more stringent.  



XXXI. ORANGE COUNTY Now Condition B.VIII. Orange County
A. 
Building And Construction Requirements Now Condition A.IX.A. with revisions 
The licensee shall comply with the building and construction requirements of Chapter 9, Orange County Code.  The licensee shall pay all appropriate fees for required building and construction permits, including inspection fees.  The licensee shall not commence operations of Unit A until it receives a Certificate of Occupancy from Orange County
B. 
Conservation Area  
Prior to initiation of construction (including any impacts to wetlands), the licensee shall have a formal conservation area determination approved by Orange County. 





















D. 
Public Works Impacts Now Condition B.VIII.E. Public Works Impacts
1.
Licensee agrees to submit to the Orange County Public Works Department a certified maintenance of traffic plan prepared by a Professional Engineer in a form that complies with the rules, regulations, standards and criteria of the County. 

2.
Licensee and its contractors must adhere to applicable Florida Department of Transportation and Orange County regulations when transporting materials and equipment to the site. 









XXXII. DEPARTMENT OF COMMUNITY AFFAIRS Now Condition B.IX Emergency Management
The Licensee shall develop a comprehensive hurricane preparation and recovery plan for the Stanton Unit A generating unit as a component of the Stanton Energy Center. The plan shall be submitted to the Department of Community Affairs and the Orange County Office of Emergency Management no later than commencement of construction of Unit A. The Licensee shall formally update the plan every 5 years following commercial operation of Unit A or whenever an additional electrical generating unit is brought into commercial service at Stanton Energy Center and shall submit these updated versions of the plan to the Department of Community Affairs and the Orange County Office of Emergency Management. 

If the Department of Community Affairs deems the plan or any of its periodic updates not to be in compliance with the requirements of this condition, it may petition for enforcement of this condition pursuant to the Florida Electrical Power Plant Siting Act. 

History 

Certification for Unit 1 issued 12/15/82; signed by Governor Graham 
Certification for Unit 2 issued 12/17/91; signed by Governor Chiles 
Modified 04/05/93; signed by Secretary Wetherell 
Modified for Alafaya Trail Extension 07/24/95; signed by Governor Chiles 
Modified to merge certification for Unit 1 & 2 12/24/97; signed by Secretary Wetherell Modified 08/07/98; signed by Secretary Wetherell 
Supplemental Certification for Unit A 09/21/01; signed by Governor Bush 
Modified 02/24/03; signed by Siting Administrator Oven 
Modified 07/20/06; signed by Siting Administrator Oven 
Supplemental Certification for Unit B 08/17/06; Signed by Secretary Castille 
Modified 01/17/07; signed by Siting Administrator Oven 

Modified 10/03/07; signed by Siting Administrator Halpin

Modified 02/06/08; signed by Siting Administrator Halpin

Modified 02/20/08; signed by Siting Administrator Halpin

Modified 02/24/08 signed by Siting Administrator Halpin

Modified 7/24/08; signed by Siting Administrator Halpin

ATTACHMENT - FIGURE 4-2 
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�� OUC received an Industrial Wastewater Facility Permit (FL0681661-001) for the SEC on June 24, 2011.  This permit constitutes authorization to discharge water under the National Pollutant Discharge Elimination system from the makeup pond emergency overflow weir to on-site wetlands that flow to the Cowpen Branch and then to the Econlockhatchee River.  The emergency overflow weir discharge represents the only known facility surface water discharge of industrial wastewater and is now covered under the site industrial wastewater facility permit.  As a result, OUC requests that this condition be removed or replaced with a reference to the site industrial wastewater facility permit.








��OUC requests that these mitigation projects be moved to Attachment C per COC condition XXVII.C.2.  “Proposed mitigation plans submitted with the DEP ERP Application forms required in Condition A.1.a. above, or submitted and approved as part of an amendment, modification, or certification, and that are deemed acceptable by DEP, shall include applicable construction conditions, success criteria and monitoring plans, and shall be incorporated into these Conditions as Attachment C (Mitigation Plans).”  








�Conditions A-G associated with Unit 2 construction.  Construction completed 1996.


�No longer appear in the 06/17/15 version of Edition L.


�Conservation easement provided to FDEP as mitigation for Unit A construction.


�No longer appear in the 06/17/15 version of Edition L.


�Confirm this condition has been met


�This condition has been met and has been removed in the 06/17/15 version of Edition L.


�This is past permitting action that is no longer applicable.  Has been deleted in the 06/17/15 version of Edition L.


�ERP application submitted in conjunction with submittal of the Supplemental Site Certification Application on February 17, 2006.


�This is past permitting action that is no longer applicable.  Has been deleted in the 06/17/15 version of Edition L.


� Does A.XXVII adequately address this condition?   Should this remain as a specific condition.  Appears to be associated with the facility’s NPDES


�Has been deleted in the 06/17/15 version of Edition L because the language is associated with NPDES permit. 





�Confirm this condition has been met


�ERP application submitted in conjunction with submittal of the Supplemental Site Certification Application on February 17, 2006.


�This condition has been met and has been deleted in the 06/17/15 version of Edition L.


�Request to move sections O and P to the more appropriate Attachment C section of the updated COC. Both Magnolia Ranch and North Substation remain active.


�These conditions will be a part of the facility’s mitigation plan


�OUC requests that these mitigation projects be moved to Attachment C per COC condition XXVII.C.2.  “Proposed mitigation plans submitted with the DEP ERP Application forms required in Condition A.1.a. above, or submitted and approved as part of an amendment, modification, or certification, and that are deemed acceptable by DEP, shall include applicable construction conditions, success criteria and monitoring plans, and shall be incorporated into these Conditions as Attachment C (Mitigation Plans).”  





�The site’s current Industrial Wastewater Facility Permit (FL0681661-001) identifies source water for the makeup pond to include the following:  treated effluent from the Orange County Eastern Wastewater Treatment Facility, storm water runoff for the Orange County Landfill, treated effluent from an on-site package wastewater treatment plant, storm water runoff from roof and yard drains, distillate from the on-site brine concentrator, boiler blowdown, emergency overflow for the plant recycle basin, and direct precipitation to the pond.  As part of this modification, and for the purpose of consistency, OUC requests that the current COC language in regard to sources of cooling tower makeup water be replaced with a reference to the site industrial wastewater facility permit.


 


Additionally, OUC’s intention is to send construction dewatering effluent associated with lined pond expansion or replacement, along with pond liner drainage system effluent associated with groundwater suppression, to the facility makeup pond where it will be used as cooling tower makeup.  OUC requests that the language in this condition be modified to identify groundwater resulting from construction dewatering activities and groundwater resulting from any on-site wastewater pond groundwater suppression system as sources of water to the makeup pond.


�New language in B.I.B of the 06/17/15 version of Edition L.


�Past event that is no longer applicable.  Has been deleted in the 06/17/15 version of Edition L.


�Alafaya Trail extension was originally permitted with Unit 2 in 1992.  Construction has been completed.  Mitigation on-going and is part of the site RCW Management with yearly reports submitted.


�Appear in B.I.F in the 06/17/15 version of Edition L.  Language has been modified and Landfill Operations and Maintenance Plan is referenced.


�The current conditions within this section of the COC represent specific operational requirements associated with the facility solid waste landfill.  OUC requests that the specific operational requirements in sections D and E of the COC be removed/modified and replaced by incorporating a reference to the document entitled “Operation Plan for Combustion Waste Management Areas” as an attachment to the COC.  The “Operations Plan for Combustion Waste Management Areas “Management Plan  shall be implemented for the life of the landfill and is incorporated into these Conditions of Certification in Attachment __.  OUC also requests the addition of language to the COC indicating that any revisions or updates to this attachment shall be submitted to the Department’s Central District Office Solid Waste Section as appropriate for review and approval.





�Verify all conditions have been met


�Is this still applicable? 


�Language has been modified in the 06/17/15 version of Edition L.


�Change made in the 06/17/15 version of Edition L.


�Construction has been completed. This condition has been removed in the 06/17/15 version of Edition L.





�Verify this condition has been met


�Will Condition A.VIII cover this requirement


�Restoration is covered in A.VIII in the 06/17/15 version of Edition L.


�Verify this condition has been met





�Covered under A.VII.C in the 06/17/15 version of Edition L.


�Condition has been met and removed in the 06/17/15 version of Edition L.


��Verify this condition has been met; CD/OUC to review





�Condition has been met and removed in the 06/17/15 version of Edition L.


�Verify this condition has been met


�Similar to the language change request associated with Condition X.D.3, OUC received an Industrial Wastewater Facility Permit (FL0681661-001) for the SEC on June 24, 2011.  This permit constitutes authorization to discharge water under the National Pollutant Discharge Elimination system from the makeup pond emergency overflow weir to on-site wetlands that flow to the Cowpen Branch and then to the Econlockhatchee River.  The emergency overflow weir discharge represents the only known facility surface water discharge of industrial wastewater and is now covered under the site industrial wastewater facility permit.  As a result, OUC requests that this condition be removed or replaced with a reference to the site industrial wastewater facility permit.





�Conditions covered under the facility’s general conditions


�Agree.  Condition has been removed in the 06/17/15 version of Edition L.


�Conditions in this section are associated with the construction of SEC Unit 2 and are out-of-date.  This construction project was completed in 1996.


�No longer applicable per OUC


�Redundant language covered under Section IX. Cooling Tower.


�Appear in B.I.D in the 06/17/15 version of Edition L.


�Deleted per SJRWMD


�Agreement already in place.  Condition is no longer applicable and has been removed in the 06/17/15 version of Edition L.


Requirement a�lready covered in A.XXVI in the 06/17/15 version of Edition L.


�Deleted per SJRWMD


�Off-site discharge as provided for by the overflow structure in the makeup water pond covered under NPDES permit.


�Agree.  Condition has been removed in the 06/17/15 version of Edition L.


�The entire section has been deleted in the 06/17/15 version of Edition L.


�Move or delete per SJRWMD


�Dated Condition?  DOT to verify if the conditions are dated or are still applicable  


Requirement already covered �in B.II in the 06/17/15 version of Edition L.


�Deleted per OUC


Orange County should agree to deletion before final version is issued. 


�Can this section be removed from COC?  Construction of Unit B was completed


�Section has been removed in the 06/17/15 version of Edition L.


�County and OUC to decide jointly on how this is addressed.  The cooling towers are associated facilities and the agreement should be recognized in the COC.  Keeping a reference and attaching the agreement is an option.


�Agreement with Orange County and OUC is currently in place, condition out of date.


�Condition is outdated and has been removed in the 06/17/15 version of Edition L.


�Deleted per OUC


�Condition is outdated and has been removed in the 06/17/15 version of Edition L.


�Project has been completed and condition no longer applicable.
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